## Fittings
AMPLATS PIPING SPECIFICATIONS - FITTINGS (ALL SPECS)
Spec | Size Range | Description | Material | Drawing/Standard
V2 | 50&UNDER | MI, SCRD AND BANDED TO STD DRG JAA00045306 SHTS 1-20 | SABS 509 | JAA00045306
V2 | 65-150 | CS STD WT, BW TO STD DRG JAA00045304 SHEETS 1 & 2 | BS 1640 GRD WPB | JAA00045304
V2 | 200-700 | TO STANDARD DRAWING JAA00045300 SHEETS 5 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 6mm WALL | JAA00045300/301
A2 | 15-150 | TO STANDARD DRAWING JAA00045303 SHEETS 5,6,9 TO 19 | SABS 62 MED WT SCARFED | JAA00045303
A2 | 200-700 | TO STANDARD DRAWING JAA00045301 SHEETS 4 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
BA | 8-40 | WROUGHT ST. SCRD TO ISO R7, DIM'S TO BS 1740 | BS 1387 | JAA00045310
BA | 50-150 | BW LR (1.5D) ELBOW 90/45 SCH 40 DIM'S TO ANSI B16.9 | ASTM A234-WPB | JAA00045304
BA | 200-500 | BW LR (1.5D) ELBOW 90/45 SCH 10 DIM'S TO ANSI B16.9 | SABS 719 GRD "B" 6mm WALL | JAA00045304
BA | 15-150 | BW CAP SCH 40/20/10 DIM'S TO ANSI B16.9 | ASTM A234-WPB | JAA00045304
BA | 8-40 | HALF COUPLING 3000# SCRD TO ISO R7 DIM'S TO ANSI B16.11 | ASTM A105
BA | 8-40 | WROUGHT ST. SCRD TO ISO R7 DIM'S TO BS 1740 (HEX BUSH, NIPPLE, PLUG) | BS 1387
BA | 50-500 | BW REDUCER CONC/ECC SCH 40/20/10 DIM'S TO ANSI B16.9 | ASTM A234-WPB / SABS 719 | JAA00045304
BA | 8-40 | WROUGHT ST. SCRD TO ISO R7 DIM'S TO BS 1740 (SOCKET, TEE) | BS 1387
BA | 50-500 | BW TEE EQUAL/REDUCING SCH 40/20/10 DIM'S TO ANSI B16.9 | ASTM A234-WPB / SABS 719 | JAA00045304
EA | 50-300 | CAP SCHEDULE 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-304L
EA | 15-40 | BW LR (1.5D) SCHED 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-304L
EA | 50-300 | BW LR (1.5D) SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-304L
EA | 15-40 | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F304L
EA | 15-40 | SCRD TO ISO R7 HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F304L
EA | 15-40 | NIPPLE SCHEDULE 80S 80mm LONG / THREAD (ISO R7) ON ONE END 80mm LONG | ASTM A403-WP-304L / ASTM A182-F304L
EA | 15-40 | PLUG SQUARE HEAD SCRD DIM'S TO ANSI B16.11 | ASTM A182-F304L
EA | 15-40 | CONC/ECC SCH 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-304L
EA | 50-300 | CONC/ECC SCH 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-304L
EA | 15-40 | BW TEE SCHED 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-304L
EA | 50-300 | BW TEE SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-304L
EA | 15-40 | SOCKOLET CLASS 3000# 316L SS DIM'S TO DRG IAC 00045304 2/3 | ASTM A182-F304L
EA | 15-40 | WELDOLET SCHED 40S DIM'S TO DRG IAC00045304 3/3 | ASTM A403-WP-304L
JA | 140-225 (OD) | MOULDED PN10 FOR BUTT WELDING DIM'S DRG JAA XXXXXXXXX X REF: GF 27.01.09 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 250-400 (OD) | MOULDED PN10 FOR BUTT WELDING DIM'S DRG JAA XXXXXXXXX X REF: AGRU 01 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 20-110 (OD) | MOULDED END CAP FOR SOCKET FUSION PN10 DIM'S JAAXXXXXXXX X REF: GF 27.96.01 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 20-110 (OD) | MOULDED PN10 FOR SOCKET FUSION DIM'S DRG JAAXXXXXXXX X REF: GF 27.10.01 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 125-225 (OD) | MOULDED PN10 FOR BUTT WELDING DIM'S DRG JAAXXXXXXXX X REF: AGRU 60 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 20-110 (OD) | MOULDED PN10 FOR SOCKET FUSION DIM'S DRG JAAXXXXXXXX X REF: GF 27.91.03 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 75-225 (OD) | MOULDED PN10 FOR BUTT WELDING DIM'S DRG JAAXXXXXXXX X REF: GF 27.09.09 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 160-400 (OD) | MOULDED PN10 FOR BUTT WELDING DIM'S DRG JAAXXXXXXXX X REF: AGRU 07 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 20-110 (OD) | MOULDED PN10 FOR SOCKET FUSION DIM'S DRG JAAXXXXXXXX X REF: GF 27.20.01 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 140-225 (OD) | MOULDED PN10 FOR BUTT WELDING DIM'S DRG JAAXXXXXXXX X REF: GF 27.20.09 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 250-400 (OD) | REINFORCED MOULDED PN10 FOR BUTT WELDING DRG JAAXXXXXXXX X REF: AGRU 06 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 125-250 (OD) | REINFORCED MOULDED PN10 FOR BUTT WELDING DRG JAAXXXXXXXX X REF: AGRU 16 | POLYPROPYLENE (CO-POLYMER) SABS 1315
AA2 | 15-150 | TO STANDARD DRAWING JAA00045303 SHEETS 5,6,9 TO 19 | SABS 62 MED WT | JAA00045303
AA2 | 200-700 | TO STANDARD DRAWING JAA00045301 SHEETS 4 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
AF2 | 15-150 | TO STANDARD DRAWING JAA00045303 SHEETS 5,6,9 TO 19 | SABS 62 MED WT | JAA00045303
AF2 | 200-450 | TO STANDARD DRAWING JAA00045301 SHEETS 4 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
BB | 15-40 | SOCKET WELD ELBOW CLASS 3000# TO ANSI B16.11 | ASTM A105
BB | 50-200 | BW LR (1.5D) ELBOW SCHED 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BB | 15-40 | SOCKET WELD HALF/FULL CPLG 3000# DIM'S TO ANSI B16.11 | ASTM A105
BB | 15-40 | NIPPLE SCHEDULE 80 THREAD (ISO R7) ON ONE END 80mm LONG | ASTM A106 GR B
BB | 15-40 | PLUG SQUARE HEAD SCRD TO ISO R7 DIM'S TO ANSI B16.11 | ASTM A105
BB | 15-50 | SOCKET WELD CONCENTRIC/ECCENTRIC 3000# DIM'S TO ANSI B16.11 | ASTM A105
BB | 65-200 | BW CONCENTRIC/ECCENTRIC SCH 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BB | 15-40 | SOCKET WELD TEE CLASS 3000# DIM'S TO ANSI B16.11 | ASTM A105
BB | 50-200 | BW TEE SCHED 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
P2 | ALL SIZES | uPVC FITTINGS TO SABS 966 CLASS 9, SOLVENT CEMENT SOCKET | SABS 966
K1 | 63-500 | HDPE FITTINGS, BUTT FUSION / ELECTROFUSION TO SANS ISO 4427 | PE80 | SANS ISO 4427
G2 | 65&UNDER | CS, MED WT, ENDS SCREWED TO BSP | SABS 62 GALVANISED
G2 | 80-150 | CS, MED WT, BE | SABS 62 GALVANISED
G2 | 200-700 | CS, 6mm WALL, PE, ERW | SABS 719 GRD "B"
A4 | 50-80 | SCHEDULE 40 SEAMLESS, FLANGED MALE/FEMALE REINFORCED ON THE WEAR FACE, RADIUS = 800 | ASTM A106 GRD B
A4 | 100-125 | SCHEDULE 40 SEAMLESS, FLANGED MALE/FEMALE REINFORCED ON THE WEAR FACE, RADIUS = 1500 | ASTM A106 GRD B
A4 | 150 | SCHEDULE 40 SEAMLESS, FLANGED MALE/FEMALE REINFORCED ON THE WEAR FACE, RADIUS = 1800 | ASTM A106 GRD B
A4 | 200 | SCHEDULE 40 SEAMLESS, FLANGED MALE/FEMALE REINFORCED ON THE WEAR FACE, RADIUS = 2000 | ASTM A106 GRD B
A4 | 80-125 | BARREL BEND, 8mm WALL THICKNESS, 400mm DIAMETER, 280-400 WIDE | SABS 1431-300 WA
A4 | 150-175 | BARREL BEND, 8mm WALL THICKNESS, 600mm DIAMETER, 450 WIDE | SABS 1431-300 WA
A4 | 200-250 | BARREL BEND, 10mm WALL THICKNESS, 700mm DIAMETER, 550-630 WIDE | SABS 1431-300 WA
A4 | 300-350 | BARREL BEND, 10mm WALL THICKNESS, 800mm DIAMETER, 690-750 WIDE | SABS 1431-300 WA
A4 | 50-300 | BW CONCENTRIC SCH 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
A4 | 50-300 | BW TEE SCHED 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
ED | 15-40 | BW SCHEDULE 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-316L
ED | 50-100 | BW SCHEDULE 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-316L
ED | 15-40 | BW LR (1.5D) SCHED 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-316L
ED | 50-100 | BW LR (1.5D) SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-316L
ED | 150-300 | BW SR (1D) MITRE BEND FABRD FROM PIPE SCHED 5S | ASTM A312 GR TP 316L | JAA00045300
ED | 350-600 | BW SR (1D) MITRE BEND FABRD FROM PIPE SCHED 5S | ASTM A240 GR 316L | JAA00045300
ED | 15-40 | SCRD TO ISO R7 HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
ED | 15-40 | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
ED | 15-40 | NIPPLE SCHEDULE 40S 80mm LONG / THREAD (ISO R7) ON ONE END 80mm LONG | ASTM A403-WP-316L / ASTM A182-F316L
ED | 15-40 | PLUG SQUARE HEAD SCRD DIM'S TO ANSI B16.11 | ASTM A182-F316L
ED | 15-50 | BW CONCENTRIC/ECCENTRIC SCH 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-316L
ED | 50-150 | BW CONCENTRIC/ECCENTRIC SCH 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-316L
ED | 150-300 | BW FAB. FROM PIPE SCHED 5S CONC & ECC DIM'S TO ANSI B16.9 | ASTM A312 GR TP 316L
ED | 350-600 | BW FAB. FROM PIPE SCHED 5S CONC & ECC DIM'S TO ANSI B16.9 | ASTM A240 GR 316L
ED | 150-600 | BW LAP JOINT STUB END SCH 5S TYPE A MSS DIM'S TO BS 1640 AND ANSI B16.9 | ASTM A403-WP-316L
ED | 15-40 | BW SCHED 40S DIM'S TO ANSI B16.9 (TEE) | ASTM A403-WP-316L
ED | 50-100 | BW SCHED 10S DIM'S TO ANSI B16.9 (TEE) | ASTM A403-WP-316L
ED | 150-300 | BW FABRD FROM PIPE SCHED 5S DIM'S TO ANSI B16.9 (TEE) | ASTM A312 GR TP 316L
ED | 350-600 | BW FABRD FROM PIPE SCHED 5S DIM'S TO ANSI B16.9 (TEE) | ASTM A240 GR 316L
I2 | 15-50 | SOCKET WELD CUP CLASS 3000# TO ANSI B16.11 | ALLOY 20 / ASTM B464
I2 | 80-900 | DUCTILE IRON FLANGED CAPS CLASS 150#, DIM'S TO ANSI B16.42, TABLE 4 | ASTM A536, Gr. 70-50-5
I2 | 15-50 | SOCKET WELD ELBOW CLASS 3000# TO ANSI B16.11 | ALLOY 20 / ASTM B464
I2 | 80-900 | DUCTILE IRON FLANGED BENDS, DIM TO ANSI/AWWA C110/A21.10-1993, TABLE 10.16 | ASTM A536, Gr. 70-50-5
I2 | 15-50 | SOCKET WELD FULL CPLG 3000# DIMENSIONS TO ANSI B16.11 | ALLOY 20 / ASTM B464
I2 | 15-50 | SOCKET WELD CONCENTRIC/ECCENTRIC 3000# DIM'S TO ANSI B16.11 | ALLOY 20 / ASTM B464
I2 | 80-900 | DUCTILE IRON FLANGED CONCENTRIC REDUCERS, CLASS 250#, DIM'S TO ANSI/AWWA | ASTM A536, Gr. 70-50-5
I2 | 15-50 | SOCKET WELD TEE CLASS 3000# DIM'S TO ANSI B16.11 | ALLOY 20 / ASTM B464
I2 | 80-900 | DUCTILE IRON FLANGED TEE, DIM'S TO ANSI/AWWA C110/A21.10-1993, TABLE 10.17 | ASTM A536, Gr. 70-50-5
I2 | 15-50 | LAP-JOINT STUB-END, DIM'S TO ANSI B16.9-TABLE A7 | ALLOY 20 / ASTM B464
MB | 25-150 | DUCTILE IRON 90/45 ELBOW RF CLASS 150# TO ANSI B16.42, PVDF LINED 2.7mm THICK | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 50-150 | CS FF 3D FLANGED BEND, PVDF LINED 2.7mm THICK C/W TWO SLIP-ON FLG'S | BEND SABS 62 MEDIUM / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | DUCTILE IRON EQUAL TEE RF CLASS 150# TO ANSI B16.42, PVDF LINED | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | DUCTILE IRON REDUCING TEE RF CLASS 150# TO ANSI B16.42, PVDF LINED | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | DUCTILE IRON EQUAL CROSS RF CLASS 150# TO ANSI B16.42, PVDF LINED | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | DUCTILE IRON CONC/ECC RED. RF CLASS 150# TO ANSI B16.42, PVDF LINED | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | DUCTILE IRON RED. FLANGE RF CLASS 150# DRILLED AND TAPPED, PVDF LINED | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | DUCTILE IRON INSTRUMENT TEE WITH ONE NOZZLE RF CLASS 150#, PVDF LINED | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | DUCTILE IRON INSTRUMENT TEE WITH TWO NOZZLES AT 90 RF CLASS 150#, PVDF LINED | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | DUCTILE IRON LATERAL 45 RF CLASS 150# TO ANSI B16.42, PVDF LINED | D. IRON SABS GRADE SG 42 / PVDF ASTM D 638 BLUE | JAA00045300
MB | 25-150 | PVDF SPACER 75mm LONG FABD AND DIM'S TO DRG JAA00045350 | PVDF ASTM D 638 BLUE
O1 | 15-40 | CAP SCRD CL 3000 DIM'S TO ANSI B16.11 | ASTM A182 F316L
O1 | 15-40 | CAP BW SCHED 40S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 50-150 | CAP BW SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 15-40 | ELBOW 90 deg BW SCHED 40S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 50-150 | ELBOW 90 deg BW SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 15-40 | ELBOW 45 deg BW SCHED 40S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 50-150 | ELBOW 45 deg BW SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 15-40 | HALF COUPLING SCRD CL 3000 DIM'S TO ANSI B16.11 | ASTM A182 Gr. F316L
O1 | 15-40 | NIPPLE SCHED 40S PLAIN BOTH ENDS 80mm LONG | ASTM A182 Gr. F316L
O1 | 15-40 | NIPPLE SCHED 40S THREAD ONE END 80mm LONG | ASTM A182 Gr. F316L
O1 | 15-40 | PLUG SQUARE HEAD SCRD DIM'S TO ANSI B16.11 | ASTM A182 Gr. F316L
O1 | 50-150 | REDUCER CONC. BW SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 50-150 | REDUCER ECC. BW SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 15-40 | SWAGE NIPPLE PLAIN BOTH ENDS (BW-BW) SCHED 40S | ASTM A182 F316L / ASTM A403 WP 316L
O1 | 15-40 | TEE BW SCHED 40S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 50-150 | TEE BW SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 50-150 | TEE RED BW SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403 WPS 316L
O1 | 15-40 | WELDOLET SCHED 40S DIM'S TO MSS SP-97 | ASTM A182 Gr. F316L
S3 | 15-300 | SEAMLESS, BW, L.R., SCH 40S, DIM TO ANSI B16.9 (BENDS, TEE, REDUCER) | ASTM A403 Gr. WP 316L
S3 | 15-40 | SOCKET WELD, 3000#, DIM TO ANSI B16.11 (HALF COUPLING) | ASTM A182 Gr. F316L
S3 | 15-40 | SCREWED ISO R7, 3000#, DIM TO ANSI B16.11 (HALF COUPLING, PLUGS) | ASTM A182 Gr. F316L
S3 | 15-300 | SEAMLESS, BW, SCH 40S, DIM TO ANSI B16.9 (END CAPS) | ASTM A403 Gr. WP 316L
A5 | 8-32 | M.C.I. BEND 90/45 FEM/FEM SCRD TO SABS 1109 | SABS 509
A5 | 8-32 | HEX HEAD BUSHING, SCRD TO SABS 1109 | SABS 509
A5 | 8-32 | M.C.I. CAPS, SCRD TO SABS 1109 | SABS 509
A5 | 40-500 | CAP BW SCHED STD DIM'S TO ANSI B16.9 | ASTM A234 WPB
A5 | 8-32 | WROUGHT STEEL COUPLING SCRD TO SABS 1109 | ASTM A106 B
A5 | 8-32 | HALF COUPLING SCRD TO SABS 1109, CL. 3000 DIM'S TO ANSI B16.11 | ASTM A105
A5 | 8-32 | M.C.I. RED. ELBOW FEM/FEM, SCRD TO ANSI B2.1, CL 150 | SABS 509
A5 | 40-500 | ELBOW 45/90 deg BW SCHED STD DIM'S TO ANSI B16.9 | ASTM A234 WPB
A5 | 8-32 | BARREL NIPPLE SCRD TO SABS 1109 80mm LONG SCHED.80 | ASTM A106 B
A5 | 8-32 | HEX HEAD PLUG, SCRD TO SABS 1109 | SABS 509
A5 | 40-500 | REDUCER CONC/ECC. BW SCHED STD DIM'S TO ANSI B16.9 | ASTM A234 WPB
A5 | 8-32 | M.C.I. SOCKET (COUPLING) SCRD TO SABS 1109 | SABS 509
A5 | 8-32 | SWAGE NIPPLE THREAD SMALL END (BW-SCRD) SCHED XS | ASTM A234 WPB
A5 | 40-500 | TEE BW SCHED STD DIM'S TO ANSI B16.9 | ASTM A105
A5 | 8-32 | M.C.I. TEE, FEM/FEM/FEM SCRD TO SABS 1109 | SABS 509
A5 | 40-500 | TEE RED BW SCHED STD DIM'S TO ANSI B16.9 | ASTM A234 WPB
AL2 | 150&UNDER | TO STD DRG JAA00045303 SHEETS 5, 6 AND 9 TO 19 | SABS 62 MED WT | JAA00045303
AL2 | 200-450 | TO STD DRG JAA00045301 SHTS 5 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
AL2 | 500-600 | TO STD DRG JAA00045301 SHTS 5 TO 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
BF2 | 50-300 | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS) | BS1640 GRD WPB SCH 40
C4 | 200-450 | TO STANDARD DRAWING JAA00045301 SHEETS 5, 6, 7 & 8 | SABS 719 GRD "C", CS 8mm WALL | JAA00045301
EB | 15-40 | CAP BW, SCHED 40S, DIM'S TO ASME B16.9 | ASTM A403-WP-WX-31
EB | 50-350 | CAP BW SCHEDULE 10S DIM'S TO ASME B16.9 | ASTM A403-WP-WX-31
EB | 15-40 | BW LR (1.5D) SCHED 40S DIM'S TO ASME B16.9 | ASTM A403-WP-WX-31
EB | 50-250 | BW LR (1.5D) SCHED 40S DIM'S TO ASME B16.9 (ABRASIVE SLURRY) | ASTM A403-CR (ABRASIVE SLURRY)
EB | 50-350 | BW LR (1.5D) SCHED 10S DIM'S TO ASME B16.9 | ASTM A403-WP-WX-31
EB | 15-40 | 3D PULLED BEND 40S | ASTM A312 GR TP 316L
EB | 15-40 | SOCKET WELD HALF CPLG CL 3000, DIMENSIONS TO ASME B16.11 | ASTM A182-F316L
EB | 15-40 | SCRD TO ISO R7 HALF CPLG CL 3000, DIMENSIONS TO ASME B16.11 | ASTM A182-F316L
EB | 15-40 | NIPPLE SCHEDULE 80S, PLAIN BOTH ENDS, 80mm LONG | ASTM A312 GR TP 316L
EB | 15-40 | NIPPLE SCHEDULE 80 THREAD (SABS 1109) ON ONE END 80mm LONG | ASTM A182-F316L
EB | 15-40 | PLUG SQUARE HEAD SCRD DIM'S TO ASME B16.11 | ASTM A182-F316L
EB | 15-40 | CONC/ECC SCH 40S DIM'S TO ASME B16.9 | ASTM A403-WP-WX-31
EB | 50-250 | CONC/ECC SCH 40S DIM'S TO ASME B16.9 (ABRASIVE SLURRY) | ASTM A403-CR (ABRASIVE SLURRY)
EB | 50-350 | CONC/ECC SCH 10S DIM'S TO ASME B16.9 | ASTM A403-WP-WX-31
EB | 15-40 | SOCKOLET CL 3000, 316L SS DIM'S TO MSS SP-97 | ASTM A182-F316L
EB | 15-40 | BW TEE SCHED 40S DIM'S TO ASME B16.9 | ASTM A403-WP-WX-31
EB | 50-250 | BW TEE SCHED 40S DIM'S TO ASME B16.9 (ABRASIVE SLURRY) | ASTM A403-CR (ABRASIVE SLURRY)
EB | 50-350 | BW TEE SCHED 10S DIM'S TO ASME B16.9 | ASTM A403-WP-WX-31
EB | 15-40 | WELDOLET SCHED 40S DIM'S TO MSS SP-97 | ASTM A182-F316L
F2 | 80-150 | SEE NOTES 2 & 3 CS, STD WT, BW | BS 1460 GRADE WPB
F2 | 200-600 | CS, 6mm WALL, PE (BENDS 2-D RADIUS) | SABS 719 GRADE "B"
G2A | 15-65 | TO STANDARD DRAWING JAA00045303 SHEETS 5,6,9 TO 19 | SABS 62 MED WT SCARFED | JAA00045303
V2A | 50 | CS STD WT, BW TO STD DRG JAA00045304 SHEETS 1 & 2 | BS 1640 GRD WPB | JAA00045304
V7 | 50&UNDER | WROUGHT STEEL, SCRD TO STD DRG JAA00045310 SHTS 1-12 | BS 1740 | JAA00045310
V7 | 65-150 | CS STD. WT, BW TO STD DRG JAA00045304 SHEETS 1 & 2 (BS 1640) | BS 1640 GRD WPB | JAA00045304
V7 | 200-700 | FABRICATED TO STANDARD DRAWING JAA00045300 SHEETS 5 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 10mm WALL | JAA00045300/301
AA5 | 150&UNDER | TO STD DRG JAA00045303 SHEETS 5, 6 AND 9 TO 19 | SABS 62 MED WT | JAA00045303
AA5 | 200-450 | TO STD DRG JAA00045301 SHTS 4 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
AA5 | 500-600 | TO STD DRG JAA00045301 SHTS 4 TO 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
BC | 15-50 | BW CAP SCH 80 TO ANSI B16.9 | ASTM A234 WPB
BC | 80-200 | BW CAP SCH 40 TO ANSI B16.9 | ASTM A234 WPB
BC | 15-50 | BW LR (1.5D) ELBOW SCHED 80 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BC | 80-200 | BW LR (1.5D) ELBOW SCHED 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BC | 15-50 | NIPPLE SCHEDULE 80 PLAIN BOTH ENDS 80mm LONG | ASTM A106 GR B
BC | 15-50 | BW CONCENTRIC/ECCENTRIC SCH 80 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BC | 80-200 | BW CONCENTRIC/ECCENTRIC SCH 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BC | 15-50 | BW TEE SCHED 80 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BC | 80-200 | BW TEE SCHED 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BC | 15-50 | WELDOLET SCHED 80 DIM'S TO JAC00045304 3/3 | ASTM A105
E2 | 100-250 | SEE NOTE 2 (ALL FITTINGS SHALL BE DESIGNED AS FLANGED SPECIALS) | ASTM A106 GRADE "B"
E7 | 200-500 | SEE NOTE 2 (ALL BENDS & FITTINGS SHALL BE DESIGNED AS SPECIALS) | SABS 719 GRADE "B"
EC | 50-300 | CAP SCHEDULE 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-WX-316L
EC | 15-40 | SOCKET WELD 3000# DIM'S TO ANSI B16.11 | ASTM A182-F316L
EC | 50-300 | BW LR (1.5D) SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-WX-316L
EC | 15-40 | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
EC | 15-40 | SCRD TO ISO R7 HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
EC | 15-40 | NIPPLE SCHEDULE 80S 80mm LONG | ASTM A403-WP-WX-316L
EC | 15-40 | NIPPLE SCHEDULE 80 THREAD (ISO R7) ON ONE END 80mm LONG | ASTM A182-F316L
EC | 15-40 | PLUG SQUARE HEAD SCRD DIM'S TO ANSI B16.11 | ASTM A182-F316L
EC | 15-40 | CONC/ECC SCH 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-WX-316L
EC | 50-300 | CONC/ECC SCH 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-WX-316L
EC | 15-40 | SOCKET WELD 3000# DIM'S TO ANSI B16.11 (TEE) | ASTM A182-F316L
EC | 50-300 | BW TEE SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-WX-316L
EC | 15-40 | SOCKOLET 3000# 316L SS DIM'S TO DRG IAC 00045304 2/3 | ASTM A182-F316L
EC | 15-40 | WELDOLET SCHED 40S DIM'S TO DRG IAC00045304 3/3 | ASTM A403-WP-WX-316L
EH | 50-300 | CAP SCHEDULE 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-304
EH | 350-500 | CAP SCHEDULE 5S DIM'S TO ANSI B16.9 | ASTM A403-WP-304
EH | 15-40 | BW LR (1.5D) SCHED 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-304
EH | 50-150 | BW LR (1.5D) SCHED 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-304
EH | 200-300 | BW SR (1D) MITRE BEND FABRD FROM PIPE SCHED 10S | ASTM A312 GR TP 304 | JAA00045300
EH | 350-500 | BW SR (1D) MITRE BEND FABRD FROM SCHED 5S | ASTM A240 TYPE 304 | JAA00045300
EH | 15-40 | HPCPLG 3000# SOCKET WELD DIMENSIONS TO ANSI B16.11 | ASTM A182-F304
EH | 15-40 | NIPPLE SCHEDULE 80S PLAIN BOTH ENDS 80mm LONG | ASTM A403-WP-304
EH | 15-40 | NIPPLE SCHEDULE 80S THREAD ON ONE END 80mm LONG | ASTM A403-WP-304
EH | 15-40 | PLUG SQUARE HEAD SCRD TO ISO R7 DIM'S TO ANSI B16.11 | ASTM A182-F304
EH | 15-50 | BW CONCENTRIC/ECCENTRIC SCH 40S DIM'S TO ANSI B16.9 | ASTM A403-WP-304
EH | 65-300 | BW CONCENTRIC/ECCENTRIC SCH 10S DIM'S TO ANSI B16.9 | ASTM A403-WP-304
EH | 350-500 | BW CONC/ECCENTRIC FABRICATED FROM PIPE SCH 5S | ASTM A240 TYPE 304 | JAA00045300
EH | 15-40 | BW SCHED 40S DIM'S TO ANSI B16.9 (TEE) | ASTM A403-WP-304
EH | 50-150 | BW SCHED 10S DIM'S TO ANSI B16.9 (TEE) | ASTM A403-WP-304
EH | 200-300 | BW FABRD FROM PIPE SCHED 10S | ASTM A312 GR TP 304 | JAA00045300
EH | 350-500 | BW FABRD FROM PIPE SCHED 5S | ASTM A240 TYPE 304 | JAA00045300
J2 | 16-110 | TO STANDARD DRAWING JAA00045308 SHEETS 3 & 6 | POLYPROPYLENE CLASS 10 SABS 1315 | JAA00045308
J2 | 125-500 | TO STANDARD DRAWING JAA00045308 SHEETS 7 & 9 | POLYPROPYLENE CLASS 10 SABS 1315 | JAA00045308
L2 | 25-150 | TO STANDARD DRAWING JAA00045309 SHEETS 1 THRU 7 | ASTM A53 GRD "B" | JAA00045309
L2 | 200&ABOVE | TO STANDARD DRAWING JAA00045301 SHEETS 5,7,8 & 9 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
X2 | 25-50 | FS CLASS 3000 SCREWED BSP | BS 3799 GRADE WPB
R4 | 50-150 | TO STANDARD DRAWING JAA00045303 SHEETS 7, 8, 11 TO 19 | SABS 62 MED WT SCARFED | JAA00045303
R4 | 200-400 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
R4 | 450 & 500 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 8 & 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
B3 | 50-150 | TO STANDARD DRAWING JAA00045305 SHEETS 3, 4 & 5 | BS1640 GRD WPB SCH 40 | JAA00045305
BD | 50-300 | BW CAP SCH 40 TO ANSI B16.9 | ASTM A234 WPB
BD | 15-40 | BW LR (1.5D) ELBOW SCHED 80 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BD | 50-300 | BW LR (1.5D) ELBOW SCHED 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BD | 15-40 | NIPPLE SCHEDULE 80 PLAIN BOTH ENDS 80mm LONG | ASTM A106 GR B
BD | 15-50 | BW CONCENTRIC/ECCENTRIC SCH 80 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BD | 65-300 | BW CONCENTRIC/ECCENTRIC SCH 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BD | 15-40 | BW TEE SCHED 80 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BD | 50-300 | BW TEE SCHED 40 DIM'S TO ANSI B16.9 | ASTM A234 WPB
BD | 15-40 | WELDOLET SCHED 80 DIM'S TO JAC00045304 3/3 | ASTM A105
E5 | 200-500 | SEE NOTE 2 (ALL BENDS & FITTINGS SHALL BE DESIGNED AS SPECIALS) | SABS 719 GRADE "B"
JB | 20-160 (OD) | MOULDED PN16 FOR SOCKET FUSION DIM'S TO DIN 8063/5 REF: GF 35.96.01 | PVDF - POLYVINYLIDENE FLUORIDE
JB | 20-110 (OD) | MOULDED PN16 FOR SOCKET FUSION DIM'S TO DIN 8063/5 REF: GF 35.10.01 | PVDF - POLYVINYLIDENE FLUORIDE
JB | 20-110 (OD) | MOULDED PN16 FOR SOCKET FUSION DIM'S TO DIN 8063/5 REF: GF 35.15.01 | PVDF - POLYVINYLIDENE FLUORIDE
JB | 20-110 (OD) | MOULDED PN10 FOR SOLVENT SOCKET FUSION DIM'S DRG JAXXXXXXXX X REF: GF 35.91.03 | PVDF - POLYVINYLIDENE FLUORIDE
JB | 20-110 (OD) | MOULDED PN16 FOR SOCKET FUSION DIM'S TO DIN 8063/5 REF: GF 35.91.01 | PVDF - POLYVINYLIDENE FLUORIDE
JB | 20-110 (OD) | EQUAL MOULDED PN16 FOR SOCKET FUSION DIM'S TO DIN 8063/5 REF: GF 35.20.01 | PVDF - POLYVINYLIDENE FLUORIDE
E3 | 100-250 | SEE NOTE 2 (ALL FITTINGS SHALL BE DESIGNED AS FLANGED SPECIALS) | ASTM A106 GRADE "B"
JC | 20-63 (OD) | MOULDED PN12.5 FOR SOLVENT CEMENT WELDING, DIM'S TO ISO727&DIN 8063/5 | ABS
JC | 20-110 (OD) | MOULDED PN12.5 FOR SOLVENT CEMENT WELDING, DIM'S TO ISO727&DIN 8063/5 | ABS
JC | 20-110 (OD) | MOULDED PN12.5 FOR SOLVENT CEMENT WELDING, DIM'S TO ISO727&DIN 8063/5 (REDUCER) | ABS
JC | 20-110 (OD) | MOULDED PN12.5 FOR SOLVENT CEMENT WELDING, DIM'S TO ISO727&DIN 8063/5 (SOCKET) | ABS
JC | 20-63 (OD) | MOULDED PN12.5 FOR SOLVENT CEMENT WELDING, DIM'S TO ISO727&DIN 8063/5 WITH "O" RING GASKET | ABS & CHLOROPRENE RUBBER
JC | 20-110 (OD) | MOULDED PN12.5 FOR SOLVENT CEMENT WELDING, DIM'S TO ISO727&DIN 8063/5 (TEE) | ABS
JC | 20-63 (OD) | MOULDED PN12.5 FOR SOLVENT CEMENT WELDING, DIM'S TO ISO727&DIN 8063/5 (TEE RED) | ABS
JM | 20-160 (OD) | (2.5D) MOULDED PN6 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.00.01 | UPVC SABS 966
JM | 20-160 (OD) | MOULDED END CAP PN6 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.96.01 | UPVC SABS 966
AF3 | 15-150 | TO STANDARD DRAWING JAA00045303 SHEETS 5,6 & 9 TO 19 | SABS 62 MED WT | JAA00045303
AF3 | 200-450 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B" CS 6mm WALL | JAA00045301
AF3 | 500-600 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B" CS 8mm WALL | JAA00045301
BE | 15-40 | CAP SCRD TO ISO R7 CL3000, DIM'S TO ASME B16.11 | ASTM A105
BE | 15-40 | CAP SOCKET WELD CL 3000, DIM'S TO ASME B16.11 | ASTM A105
BE | 50-150 | CAP BW SCHEDULE 40 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 200-300 | CAP BW SCHEDULE 20 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 350-600 | CAP BW SCHEDULE 10 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 15-40 | SOCKET WELD FULL CPLG 3000# DIMENSIONS TO ASME B16.11 | ASTM A105
BE | 15-40 | SOCKET WELD ELBOW CLASS 3000# TO ASME B16.11 | ASTM A105
BE | 50-150 | BW LR (1.5D) ELBOW SCHED 40 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 200-300 | BW LR (1.5D) ELBOW SCHED 20 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 350-600 | BW LR (1.5D) ELBOW SCHED 10 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 350-600 | BW SR (1.0D) ELBOW SCHED 10 DIM'S TO ASME B16.28 | ASTM A234 WPB
BE | 15-40 | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ASME B16.11 | ASTM A105
BE | 15-40 | HALF CPLG SCRD TO ISO R7 3000# DIMENSIONS TO ASME B16.11 | ASTM A105
BE | 15-40 | NIPPLE SCHEDULE 80 PLAIN BOTH ENDS 80mm LONG | ASTM A106 GR B
BE | 15-40 | NIPPLE SCHEDULE 80 THREAD ONE END 80mm LONG | ASTM A106 GR B
BE | 15-40 | PLUG SQUARE HEAD SCRD TO ISO R7 DIM'S TO ASME B16.11 | ASTM A105
BE | 15-50 | REDUCER SOCKET WELD CONCENTRIC CL 3000 DIM'S TO ASME B16.11 | ASTM A105
BE | 50-150 | REDUCER CONCENTRIC/ECCENTRIC BW. SCHED. 40 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 200-300 | REDUCER CONCENTRIC/ECCENTRIC BW. SCHED. 20 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 350-600 | REDUCER CONCENTRIC/ECCENTRIC BW. SCHED. 10 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 15-40 | SOCKOLET CLASS 3000 DIM'S TO MSS SP-97 | ASTM A105
BE | 15-40 | SOCKET WELD TEE CLASS 3000, DIM'S TO ASME B16.11 | ASTM A105
BE | 50-150 | EQUALTEE BW SCHED 40 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 200-300 | EQUALTEE BW SCHED 20 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 350-600 | EQUALTEE BW SCHED 10 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 50-150 | REDUCING TEE BW SCHED 40 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 200-300 | REDUCING TEE BW SCHED 20 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 350-600 | REDUCING TEE BW SCHED 10 DIM'S TO ASME B16.9 | ASTM A234 WPB
BE | 15-40 | ECC/CONC SWAGE NIPPLE PLAIN BOTH ENDS (SW-SW) SCHED 80 | ASTM A234 WPB
BE | 15-50 | ECC/CONC SWAGE NIPPLE PLAIN SMALL END (BW-SW) SCHED 80 | ASTM A234 WPB
BE | 15-40 | WELDOLET SCHED 80, DIM'S TO MSS SP-97 | ASTM A105
E6 | 200-500 | SEE NOTE 2 (ALL BENDS & FITTINGS SHALL BE DESIGNED AS SPECIALS) | SABS 719 GRADE "B"
EJ | 100-1600 | FABRICATED 5-MITER BEND, 1.5 D WITH WELDED PLATE FLANGES | ASTM A240 Grade 304 PLATE
EJ | 50-150 | B.W. LR (1.5D) SCHED 10S, DIM'S TO ASME B16.9 | ASTM A403-WP-304
EJ | 200-300 | B.W. SR (1.5D) MITRE BEND FABRICATED FROM PIPE SCHED 10S | ASTM A312 GR TP 304
EJ | 350-500 | B.W. SR (1.5D) MITRE BEND FABRICATED FROM PIPE SCHED 5S | ASTM A358 CL2, ASTM A240 GR TP304
EJ | 100-1600 | FABRICATED 3-MITER BEND, 1.5 D WITH WELDED PLATE FLANGES | ASTM A240 Grade 304 PLATE
EJ | 50-150 | B.W. LR (1.5D) SCHED 10S, DIM'S TO ASME B16.9 | ASTM A403-WP-304
EJ | 100-1600 | FABRICATED REDUCER WITH WELDED PLATE FLANGES | ASTM A240 Grade 304 PLATE
EJ | 50-300 | SCHEDULE 10S, SEAMLESS, DIMENSIONS TO ASME B36.19 | ASTM A312 GR TP 304
EJ | 100-1600 | FABRICATED EQUAL TEE WITH WELDED PLATE FLANGES | ASTM A240 Grade 304 PLATE
EJ | 50-300 | SCHEDULE 10S, SEAMLESS, DIMENSIONS TO ASME B36.19 | ASTM A312 GR TP 304
EJ | 100-1600 | FABRICATED REDUCING TEE WITH WELDED PLATE FLANGES | ASTM A240 Grade 304 PLATE
FC3 | 15-50 | FS, CLASS 3000, SW | BS 3799 GRD WPB
FC3 | 65 & OVER | CS, SCHED. 80 | BS 1640 GRD WPB
G2 | 65&UNDER | MI, BANDED, GALV. SCRD TO BSP TO STD DRG JAA00045306 SHEETS 1 TO 20 | SABS 509 | JAA00045306
G2 | 80-150 | TO STD DRG JAA00045303 SHTS 5,6,9 TO 19 GALV. | SABS 62 MED WT SCARFED | JAA00045303
G2 | 200-700 | TO STD DRG JAA00045301 SHEETS 5-10 GALV. | SABS 719 GRD "B" CS 6mm WALL | JAA00045301
H2 | 50-150 | TO STANDARD DRAWING JAA00045303 SHEETS 7,8,11 TO 19 | SABS 62 MED WT SCARFED | JAA00045303
H2 | 200 & OVER | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B" CS 6mm WALL | JAA00045301
JD | 25-1600 | RTRP BUTT AND OVERWRAP 90° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JD | 25-1600 | RTRP BUTT AND OVERWRAP 45° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JD | 25-1600 | RTRP BUTT AND OVERWRAP EQUAL TEE CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JD | 25-150 | RTRP BUTT AND OVERWRAP UNEQUAL TEE (REDUCED ON BRANCH) CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JD | 25-1600 | RTRP BUTT AND OVERWRAP 45° LATERAL CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JD | 200-700 | RTRP BUTT AND OVERWRAP FABRICATED REDUCING TEE FILAMENT WOUND | VINYL ESTER DERAKANE 411-45 | IAA00045376
JD | 200-700 | RTRP BUTT AND OVERWRAP FABRICATED LATERAL 45° FILAMENT WOUND | VINYL ESTER DERAKANE 411-45 | IAA00045376
JN | 20-160 (OD) | (2D) MOULDED PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.00.01 | UPVC SABS 966
JN | 225 (OD) | (0.75 D) MOULDED PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.01.01 | UPVC SABS 966
JN | 20-160 (OD) | MOULDED END CAP PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.96.01 | UPVC SABS 966
JN | 20-160 (OD) | MOULDED PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.10.01 | UPVC SABS 966
JN | 20-160 (OD) | MOULDED PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.15.01 | UPVC SABS 966
JN | 20-140 (OD) | MOULDED PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.91.03 | UPVC SABS 966
JN | 20-63 (OD) | (REDUCING SOCKET) MOULDED PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.91.01 | UPVC SABS 966
JN | 20-225 (OD) | MOULDED PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.91.01 | UPVC SABS 966
JN | 20-225 (OD) | MOULDED PN10 FOR SOLVENT SOCKET DIM'S ISO 264 REF: GF 21.20.01 | UPVC SABS 966
JN | 20-63 (OD) | MOULDED PN10 FOR SOLVENT SOCKET DIM'S DRG JAXXXXXXXX XX REF: GF 21.20.01 | UPVC SABS 966
JQ | 25-1600 | RTRP BUTT AND OVERWRAP 90° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JQ | 25-1600 | RTRP BUTT AND OVERWRAP 45° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JQ | 25-1600 | RTRP BUTT AND OVERWRAP EQUAL TEE CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JQ | 25-150 | RTRP BUTT AND OVERWRAP UNEQUAL TEE (REDUCED ON BRANCH) CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JQ | 25-1600 | RTRP BUTT AND OVERWRAP 45° LATERAL CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JQ | 200-700 | RTRP BUTT AND OVERWRAP FABRICATED REDUCING TEE FILAMENT WOUND | VINYL ESTER DERAKANE 411-45 | IAA00045376
JQ | 200-700 | RTRP BUTT AND OVERWRAP FABRICATED LATERAL 45° FILAMENT WOUND | VINYL ESTER DERAKANE 411-45 | IAA00045376
C5 | 200-450 | TO STANDARD DRAWING JAA00045301 SHEETS 5, 6, 7 & 8 | SABS 719 GRD "C", CS 10mm WALL | JAA00045301
CF2 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS) | SCHEDULE 80
E8 | 200-500 | SEE NOTE 2 (ALL BENDS & FITTINGS SHALL BE DESIGNED AS SPECIALS) | SABS 719 GRADE "B"
CL2 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
CL5 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
CF3 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
C7 | 200-450 | TO STANDARD DRAWING JAA00045301 SHEETS 5, 6, 7 & 8 | SABS 719 GRD "C", CS 14mm WALL | JAA00045301
DC3 | 15-50 | FS, CLASS 3000, SW | BS 3799 GRD WPB
DC3 | 65-450 | CS, STD WT, BW | BS 1640 GRD WPB
DC5 | 15-50 | FS, CLASS 3000, SW | BS 3799 GRD WPB
DC5 | 65-450 | CS, STD WT, BW | BS 1610 GRD WPB
E9 | 200-500 | SEE NOTE 2 (ALL BENDS & FITTINGS SHALL BE DESIGNED AS SPECIALS) | SABS 719 GRADE "B"
K2 | 63-500 | EQUAL TEE PLAIN STUB ENDS WITH GALVANISED CS BACKING RING FLANGES TO SANS 1123 | HDPE PE100 PN16 | JAA00045314
K2 | 63-500 | 45° & 60° EQUAL LATERAL, PLAIN STUB ENDS WITH GALVANISED CS BACKING RINGS | HDPE PE100 PN16 | JAA00045314
K2 | 63-500 | CONCENTRIC & ECCENTRIC REDUCER PLAIN ENDS | HDPE PE100 PN12.5 | JAA00045314
K2 | 63-500 | 90° & 45° 3D BEND, PLAIN STUB ENDS, WITH GALV CS BACKING RING FLANGES | HDPE PE 80, PN12.5 (SEAMLESS) | JAA00045314
K2 | 110-280 | 90° & 45° 2D BEND, PLAIN STUB ENDS, WITH GALV CS BACKING RING FLANGES | HDPE PE 80, PN12.5 (SEAMLESS) | JAA00045314
K2 | 315-400 | 90° & 45° 1.5D BEND, PLAIN STUB ENDS, WITH GALV CS BACKING RING FLANGES | HDPE PE 80, PN12.5 (SEAMLESS) | JAA00045314
K2 | 110-500 | 90° & 45° 5D BEND, PLAIN STUB ENDS, WITH GALV CS BACKING RING FLANGES | HDPE PE 80, PN12.5 (SEAMLESS) | JAA00045314
MA | 25-150 | ELBOW 90° CAST DUCTILE IRON, TO ASME B16.42 CLASS 150, POLYPROPYLENE LINED | CHEMIPLAST PART No MAF9025-MAF9150 OR FAB-K Fluoroline P
MA | 25-150 | ELBOW 45° CAST DUCTILE IRON, TO ASME B16.42 CLASS 150, POLYPROPYLENE LINED | CHEMIPLAST PART No MAC90025-MAC90150 OR FAB-K Fluoroline P
MC | 25-100 | ELBOW 90° FABRICATED, ELBOW SCHED 40 TO ASME B16.9, PTFE LINED | ELBOW - ASTM A234 Gr WPB, PIPE - ASTM A106 Gr B, FLANGES - ASTM A105, LINING - PTFE - ASTM D-1457, WHITE
MC | 150-200 | ELBOW 90° FABRICATED, ELBOW SCHED 40 TO ASME B16.28, PTFE LINED | ELBOW - ASTM A234 Gr WPB, PIPE - ASTM A106 Gr B, FLANGES - ASTM A105, LINING - PTFE - ASTM D-1457, WHITE
Q2 | 10-50 | POLY AGRO LDPE POLY TYPE 1 Nylon Insert Fittings | POLY AGRO LDPE POLY
R2 | 50-150 | TO STANDARD DRAWING JAA00045303 SHEETS 7, 8, 11 TO 19 | SABS 62 MED WT SCARFED | JAA00045303
R2 | 200-600 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
BF3 | 125-300 | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS) | BS1640 GRD WPB SCH 80
CF6 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
CL6 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
AL3 | 150&UNDER | TO STD DRG JAA00045303 SHEETS 5, 6 AND 9 TO 19 | SABS 62 MED WT | JAA00045303
AL3 | 200-450 | TO STD DRG JAA00045301 SHTS 4 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
AL3 | 500-600 | TO STD DRG JAA00045301 SHTS 4 TO 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
TL2 | 20-50 | TO STD DRG JAA00045305 SHEETS 4 & 5 | BS 1640 GRD WPB SCH 40 | JAA00045305
V3 | 150&UNDER | CS STD WT, BW TO STD DRG JAA00045304 SHEETS 1 & 2 | BS 1640 GRD WPB | JAA00045304
V3 | 200-450 | TO STD DRG JAA00045300 SHTS 4 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 6mm WALL | JAA00045300/301
V3 | 500-600 | TO STD DRG JAA00045300 SHTS 4 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 8mm WALL | JAA00045300/301
V4 | 65&UNDER | WS, SCRD TO STD DRG JAA00045310 SHEETS 1 TO 12 | BS 1740 | JAA00045310
V4 | 80-150 | CS, STD WT, BW, TO STD DRG JAA00045304 SHEETS 1 & 2 | BS 1640 GRD WPB | JAA00045304
V4 | 200-400 | TO STD DRG JAA00045300 SHTS 4 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 6mm WALL | JAA00045300/301
V4 | 450 | TO STD DRG JAA00045300 SHTS 4 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 8mm WALL | JAA00045300/301
Q1 | 15-80 | NYLON INSERT TYPES 433, 439, 455
Q1 | 15-50 | NYLON INSERT TYPE 441
Q1 | 15-50 | NYLON INSERT TYPE 434
B4 | 50-150 | TO STANDARD DRAWING JAA00045305 SHEETS 3, 4 & 5 | BS1640 GRD WPB SCH 80 | JAA00045305
C3 | 200-450 | TO STANDARD DRAWING JAA00045301 SHEETS 5, 6, 7 & 8 | SABS 719 GRD "C", CS 6mm WALL | JAA00045301
C6 | 200-450 | TO STANDARD DRAWING JAA00045301 SHEETS 5, 6, 7 & 8 | SABS 719 GRD "C", CS 12mm WALL | JAA00045301
CF4 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
CF5 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
CL4 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
BF | 50-200 | BW CAP SCHEDULE 40 TO ANSI B16.9 | ASTM A234 WPB
BF | 8-40 | SOCKET WELD ELBOW CLASS 3000# TO ANSI B16.11 | ASTM A105
BF | 50-200 | BW LR (1.5D) ELBOW SCHED 40 DIMS TO ANSI B16.9 | ASTM A234 WPB
BF | 8-15 | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A105
BF | 8-40 | HEX HEAD BUSHING SCRD TO ISO R7 | ASTM A105
BF | 9-40 | NIPPLE SCHEDULE 80 THREAD (ISO R7) ON ONE END 80 mm LONG | ASTM A106 GR B
BF | 9-40 | NIPPLE SCHEDULE 80 PLAIN BOTH ENDS 80mm LONG | ASTM A106 GR B
BF | 8-40 | PLUG SQUARE HEAD SCRD TO ISO R7 DIMS TO ANSI B16.11 | ASTM A105
BF | 15-50 | BW CONCENTRIC/ECCENTRIC SCH 80 DIMS TO ANSI B16.9 | ASTM A234 WPB
BF | 65-200 | BW CONCENTRIC/ECCENTRIC SCH 40 DIMS TO ANSI B16.9 | ASTM A234 WPB
BF | 8-40 | SOCKET WELD TEE CLASS 3000# DIMS TO ANSI B16.11 | ASTM A105
BF | 50-200 | BW TEE SCHED 40 DIMS TO ANSI B16.9 | ASTM A234 WPB
BF | 8-15 | SOCKET WELD UNION CLASS 3000# DIMS TO ANSI B16.11 | ASTM A105
BH | 50-150 | CAP SCHEDULE 40 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 200-300 | CAP SCHEDULE 20 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 350-500 | CAP SCHEDULE 10 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 15-40 | SOCKET WELD ELBOW CLASS 3000# DIMS TO ANSI B16.11 | ASTM A182 FII
BH | 50-150 | BW LR (1.5D) SCHED 40 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 200-300 | BW LR (1.5D) SCHED 20 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 350-500 | BW SR (1D) MITRE BEND FABRD FROM SCHED 10 DIMS TO JAA00045300 1/8 | ASTM A335 GR PII
BH | 15-40 | HPCLG 3000# SOCKET WELD DIMENSIONS TO ANSI B16.11 | ASTM A182 FII
BH | 15-40 | NIPPLE SCHEDULE 80 PLAIN BOTH ENDS 80mm LONG | ASTM A335 GR PII
BH | 15-40 | NIPPLE SCHEDULE 80 THREAD ON ONE END 80mm LONG | ASTM A335 GR PII
BH | 15-40 | PLUG SQUARE HEAD SCRD TO ISO R7 DIMS TO ANSI B16.11 | ASTM A182 FII
BH | 15-50 | BW CONCENTRIC/ECCENTRIC SCH 80 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 65-150 | BW CONCENTRIC/ECCENTRIC SCH 40 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 200-300 | BW CONCENTRIC/ECCENTRIC SCH 20 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 350-500 | BW CONC/ECCENTRIC FABRICATED FROM PIPE SCH 10 DIMS TO JAA00045300 8/9 | ASTM A335 GR PII
BH | 15-40 | SOCKET WELD 3000# DIMS TO ANSI B16.11 | ASTM A182 FII
BH | 50-150 | BW SCHED 40 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 200-300 | BW SCHED 20 DIMS TO ANSI B16.9 | ASTM A234 WPII
BH | 350-500 | BW FABRD FROM PIPE SCHED 10 DIMS TO JAA00045300 5/8 | ASTM A335 GR PII
BI | 50-500 | BW CAP SCHEDULE 40 DIMS TO ANSI B16.9 | ASTM A234 WPB
BI | 15-40 | SOCKET WELD ELBOW CLASS 3000# TO ANSI B16.11 | ASTM A105
BI | 50-150 | BW LR (1.5D) SCHED 40 DIMS TO ANSI B16.9 | ASTM A234 WPB
BI | 200-500 | BW SR (1D) MITRE BEND FABRD FROM PIPE DIMS TO JAA00045300 1/8 | SABS 719 GR B 6mm WALL
BI | 15-40 | HPCLG 3000# SOCKET WELD DIMENSIONS TO ANSI B16.11 | ASTM A105
BI | 15-40 | NIPPLE SCHEDULE 40 PLAIN BOTH ENDS 80mm LONG | ASTM A106 GR B
BI | 15-40 | NIPPLE SCHEDULE 40 THREAD ON ONE END 80mm LONG | ASTM A106 GR B
BI | 15-150 | BW CONCENTRIC/ECCENTRIC SCH 40 DIMS TO ANSI B16.9 | ASTM A234 WPB
BI | 200-300 | BW CONCENTRIC/ECCENTRIC SCH 20 DIMS TO ANSI B16.9 | ASTM A234 WPB
BI | 350-500 | BW CONC/ECCENTRIC FABRICATED FROM PIPE SCH 5S DIMS TO JAA00045300 8/9 | SABS 719 GR B 6mm WALL
BI | 15-40 | SOCKET WELD TEE CLASS 3000# DIMS TO ANSI B16.11 | ASTM A105
BI | 50-150 | BW SCHED 40 DIMS TO ANSI B16.9 | ASTM A234 WPB
BI | 200-500 | BW FABRD FROM PIPE SCHED 10S DIMS TO JAA00045300 5/8 | SABS 719 GR B 6mm WALL
BJ | 15-100 | TO ANSI B16.9, 1971, NORMALIZED C.S. ASTM A420 GR. WPL6
BJ | 150 | TO ANSI B16.9, 1971, NORMALIZED C.S. ASTM A420 GR. WPL6
BJ | 200-800 | TO ANSI B16.9, 1971, NORMALIZED C.S. ASTM A420 GR. WPL6
BL2 | 50-300 | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS) | BS1640 GRD WPB SCH 40
BL3 | 125-300 | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS) | BS1640 GRD WPB SCH 80
C8 | 200-450 | TO STANDARD DRAWING JAA00045301 SHEETS 5, 6, 7 & 8 | SABS 719 GRD "C", CS 16mm WALL | JAA00045301
CF7 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
CL7 | ALL SIZES | SEE NOTE 4 (ALL BENDS AND FITTINGS SHALL BE DESIGNED AS SPECIALS)
E4 | 200-500 | SEE NOTE 2 (ALL BENDS & FITTINGS SHALL BE DESIGNED AS SPECIALS) | SABS 719 GRADE "B"
EF | 50-300 | CAP SCHEDULE 10S DIMS TO ANSI B16.9 | ASTM A403-WP-316 L
EF | 15-40 | BW PULLED 3D BEND 40S DIMS TO DRG | ASTM A312 GR TP 316 L
EF | 50-150 | BW PULLED 3D BEND 10S DIMS TO DRG | ASTM A312 GR TP 316 L
EF | 200-300 | BW MITRE 3D BEND FABRICATED FROM PIPE 10S DIMS TO DRG | ASTM A312 GR TP 316 L
EF | 15-40 | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
EF | 15-40 | SCRD TO ISO R7 HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
EF | 15-40 | BW EQUAL/UNEQUAL LATERAL MANUF'D FROM PIPE SS 40S DIMS TO DRG | ASTM A312 GR TP 316 L
EF | 50-150 | BW EQUAL/UNEQUAL LATERAL MANUF'D FROM PIPE SS 10S DIMS TO DRG | ASTM A312 GR TP 316 L
EF | 200-300 | BW EQUAL LATERAL MANUF'D FROM PIPE SS DIMS TO DRG | ASTM A312 GR TP 316 L
EF | 15-40 | NIPPLE SCHEDULE 80S 80mm LONG | ASTM A403-WP-316 L
EF | 15-40 | PLUG SQUARE HEAD SCRD DIMS TO ANSI B16.11 | ASTM A182-F316L
EF | 15-40 | CONC/ECC SCH 40S DIMS TO ANSI B16.9 | ASTM A403-WP-316 L
EF | 50-300 | CONC/ECC SCH 10S DIMS TO ANSI B16.9 | ASTM A403-WP-316 L
EF | 15-40 | SOCKOLET 3000# 316L SS DIMS SEE DRG IAC00045304 2/3 | ASTM A182-F316L
EF | 15-40 | WELDOLET SCHED 40S DIMS SEE DRG IAC00045304 3/3 | ASTM A403-WP-316 L
EF | 15-40 | BW EQUAL/UNEQUAL TEE MANUFACTURED FROM PIPE SCHED 40S DIMS TO DRG | ASTM A312 GR TP 316 L
EF | 50-150 | BW EQUAL/UNEQUAL TEE MANUFACTURED FROM PIPE SCHED 10S DIMS TO DRG | ASTM A312 GR TP 316 L
EF | 200-300 | BW MITRE EQUAL TEE MANUFACTURED FROM PIPE SCHED 10S DIMS TO DRG | ASTM A312 GR TP 316 L
EK | 100-1600 | FABRICATED 5-MITER BEND, 1.5 D WITH VAN STONE FLANGES | Hastelloy C-276
EK | 50-150 | B.W. LR (1.5D) SCHED 10S, DIMS TO ASME B16.9 | Hastelloy C-276
EK | 200-300 | B.W. SR (1.5D) MITRE BEND FABRICATED FROM PIPE SCHED 10S | Hastelloy C-276
EK | 350-500 | B.W. SR (1.5D) MITRE BEND FABRICATED FROM PIPE SCHED 5S | Hastelloy C-276
EK | 100-1600 | FABRICATED 3-MITER BEND, 1.5 D WITH VAN STONE FLANGES | Hastelloy C-276
EK | 50-150 | B.W. LR (1.5D) SCHED 10S, DIMS TO ASME B16.9 | Hastelloy C-276
EK | 200-300 | B.W. SR (1.5D) MITRE BEND FABRICATED FROM PIPE SCHED 10S | Hastelloy C-276
EK | 350-500 | B.W. SR (1.5D) MITRE BEND FABRICATED FROM PIPE SCHED 5S | Hastelloy C-276
EK | 100-1600 | FABRICATED REDUCER WITH VAN STONE FLANGES | Hastelloy C-276
EK | 50-300 | SCHEDULE 10S, SEAMLESS, DIMENSIONS TO ASME B36.19 | Hastelloy C-276
EK | 350-500 | SCHEDULE 5S, ELECTRIC-FUSION-WELDED, BEVELLED ENDS | Hastelloy C-276
EK | 100-1600 | FABRICATED REDUCER WITH VAN STONE FLANGES | Hastelloy C-276
EK | 50-300 | SCHEDULE 10S, SEAMLESS, DIMENSIONS TO ASME B36.19 | Hastelloy C-276
EK | 350-500 | SCHEDULE 5S, ELECTRIC-FUSION-WELDED, BEVELLED ENDS | Hastelloy C-276
EK | 100-1600 | FABRICATED EQUAL TEE WITH VAN STONE FLANGES | Hastelloy C-276
EK | 50-300 | SCHEDULE 10S, SEAMLESS, DIMENSIONS TO ASME B36.19 | Hastelloy C-276
EK | 350-500 | SCHEDULE 5S, ELECTRIC-FUSION-WELDED, BEVELLED ENDS | Hastelloy C-276
EK | 100-1600 | FABRICATED REDUCING TEE WITH VAN STONE FLANGES | Hastelloy C-276
EK | 50-300 | SCHEDULE 10S, SEAMLESS, DIMENSIONS TO ASME B36.19 | Hastelloy C-276
EK | 350-500 | SCHEDULE 5S, ELECTRIC-FUSION-WELDED, BEVELLED ENDS | Hastelloy C-276
G4 | 15-600 | TO STANDARD DRAWING JAA00045305 SHEETS 4 TO 8, GALV. | BS 1640 GRD WPB | JAA00045305
G5 | 15-600 | TO STANDARD DRAWING JAA00045305 SHEETS 4 TO 8, GALV. | BS 1640 GRD WPB | JAA00045305
G6 | 50& UNDER | FS, CLASS 3000, SCR'D TO ANSI B2.1, GALVANIZED | ANSI B16.11
GA | 15-150 | MALLEABLE CAST-IRON BEDS, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | MALLEABLE CAST-IRON BRANCHES, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. TEE BRANCH (LATERAL), SCRD TO ISO R7, DIMS SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-50 | M.C.I. BUSHES, SCRD TO ISO R7, DIMS TO SABS 509 TABLE 16 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. BUSHES, SCRD TO ISO R7, DIMS TO SABS 509 TABLE 16 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | M.C.I. CAPS, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | FORGED STEEL COUPLING SCRD TO ISO R7, DIMS TO ANSI B16.11 | ASTM A105 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. CROSSES, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. ELBOW 45, FEMFEM SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. ELBOW 45, FEMMALE SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. ELBOW FEMFEM, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. ELBOW FEMMALE, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. ELBOW MALE, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | M.C.I. BARREL NIPPLE TAPER THREAD, SCRD ISO R7, DIMS TO SABS B16.11 | SABS 62 MED HOT DIP GALV'S SABS 763
GA | 15-150 | M.C.I. HEX NIPPLES, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. PLUG, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | M.C.I. REDUCING SOCKETS, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | M.C.I. RED ELBOW FEMFEM, SCRD ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | M.C.I. RED ELBOW FEMMALE, SCRD ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. SOCKETS, SCRD TO ISO R7, HOT DIP GALV'D TO SABS 763, DIMS SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-150 | M.C.I. TEES, SCRD TO ISO R7, DIMS TO SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | M.C.I. TEE INCREASING ON BRANCH, F/F, SCRD TO ISO R7, DIMS SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | M.C.I. REDUCING ON BRANCH, FEMFEMFEM SCRD ISO R7, DIMS SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GA | 15-100 | M.C.I. REDUCING TEES ON RUN, FEMFEMFEM, SCRD ISO R7, DIMS SABS 509 | SABS 509 HOT DIP GALV'S TO SABS 763
GL2 | 65&UNDER | MI, BANDED, GALV. SCRD TO BSP TO STD DRG JAA00045306 SHEETS 1 TO 20 | SABS 509 | JAA00045306
HA | 25-150 | TYPE 'PR' - CONCENTRIC - BUTTRESS ENDS TYPE 'A' | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 25-150 | TYPE 'PRE' - ECCENTRIC - BUTTRESS ENDS TYPE 'A' | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 15-150 | GLASS PIPE SPACERS TYPE SS - PLAIN ENDS (CORNING 1992-PAGE 2.2) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 15-150 | GLASS PIPE SPACERS TYPE PSS - BUTTRESS ENDS TYPE 'A' (CORNING PAGE 2.2) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 15-150 | GLASS PIPE BENDS - BUTTRESS ENDS TYPE 'A' (CORNING 1992-PAGE 2.4) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 15-150 | GLASS PIPE BENDS - BUTTRESS ENDS TYPE 'A' (CORNING 1992-PAGE 2.4) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 40-150 | GLASS PIPE REDUCING BENDS - BUTTRESS ENDS TYPE 'A' (CORNING 1992-PAGE 2.5) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 50-150 | GLASS PIPE BENDS WITH THERMOMETER BRANCH - BUTTRESS ENDS TYPE 'A' (CORNING 1992-PAGE 2.5) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 15-80 | GLASS PIPE 'U' BENDS - BUTTRESS ENDS TYPE 'A' (CORNING 1992-PAGE 2.5) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 15-50 | GLASS PIPE 'U' BEND WITH BOTTOM OUTLET - BUTTRESS ENDS TYPE 'A' (CORNING 1992-PAGE 2.5) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
HA | 15-150 | GLASS EQUAL TEE PIECES - BUTTRESS ENDS TYPE 'A' (CORNING 1992-PAGE 2.6) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
JE | 25-1600 | GRP BUTT AND OVERWRAP 90° BEND CONTACT MOULDED | QUACORR 1200 F.R. (FURANE) | IAA00045376
JE | 25-1600 | GRP BUTT AND OVERWRAP 45° BEND CONTACT MOULDED | QUACORR 1200 F.R. (FURANE) | IAA00045376
JE | 25-1600 | GRP BUTT AND OVERWRAP EQUAL TEE CONTACT MOULDED | QUACORR 1200 F.R. (FURANE) | IAA00045379
JE | 25-150 | GRP BUTT AND OVERWRAP UNEQUAL TEE (REDUCED ON BRANCH) CONTACT MOULDED | QUACORR 1200 F.R. (FURANE) | IAA00045379
JE | 25-1600 | GRP BUTT AND OVERWRAP 45° LATERAL CONTACT MOULDED | QUACORR 1200 F.R. (FURANE) | IAA00045376
JE | 200-700 | GRP BUTT AND OVERWRAP FABRICATED REDUCING TEE FILAMENT WOUND | QUACORR 1200 F.R. (FURANE) | IAA00045376
JE | 200-700 | GRP BUTT AND OVERWRAP FABRICATED REDUCING LATERAL 45° FILAMENT WOUND | QUACORR 1200 F.R. (FURANE) | IAA00045376
JH | 40-1600 | RTPR BUTT AND OVERWRAP CONCENTRIC REDUCER CONTACT MOULDED | VINYL ESTER DERAKANE 470-36 | IAA00045376
JH | 40-1600 | RTPR BUTT AND OVERWRAP ECCENTRIC REDUCER CONTACT MOULDED | VINYL ESTER DERAKANE 470-36 | IAA00045376
JO | 25-250 | RTPR BUTT AND OVERWRAP 90° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JO | 25-250 | RTPR BUTT AND OVERWRAP 45° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JO | 25-250 | RTPR BUTT AND OVERWRAP EQUAL TEE CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045379
JO | 25-150 | RTPR BUTT AND OVERWRAP UNEQUAL TEE (REDUCED ON BRANCH) CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045379
JO | 25-250 | RTPR BUTT AND OVERWRAP 45° LATERAL CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JO | 200-250 | RTPR BUTT AND OVERWRAP FABRICATED REDUCING TEE FILAMENT WOUND | VINYL ESTER DERAKANE 411-45 | IAA00045376
JO | 200-250 | RTPR BUTT AND OVERWRAP FABRICATED REDUCING LATERAL 45° FILAMENT WOUND | VINYL ESTER DERAKANE 411-45 | IAA00045376
JP | 20-110 (OD) | ELONGATED MOULDED PN10 FOR BUTT & ELECTROFUSION WELDING | HDPE SABS 533 PART II TYPE 4
JP | 125-400 (OD) | MOULDED PN6 FOR BUTT WELDING | HDPE SABS 533 PART II TYPE 4
JP | 20-110 (OD) | END CAP FOR BUTT & ELECTROFUSION WELDING PN10 | HDPE SABS 533 PART II TYPE 4
JP | 125-225 (OD) | END CAP FOR BUTT WELDING PN10 | HDPE SABS 533 PART II TYPE 4
JP | 20-110 (OD) | ELONG. MOULD. PN10 FOR BUTT & ELECTROF. WELDING | HDPE SABS 533 PART II TYPE 4
JP | 20-110 (OD) | ELONG. MOULD. PN10 FOR BUTT & ELECTROF. WELDING | HDPE SABS 533 PART II TYPE 4
JP | 125-225 (OD) | ELONG. MOULDED PN6 FOR BUTT WELDING | HDPE SABS 533 PART II TYPE 4
JP | 75-125 (OD) | MOULDED PN10 FOR BUTT WELDING | HDPE SABS 533 PART II TYPE 4
JP | 160-430 (OD) | MOULDED PN6 FOR BUTT WELDING | HDPE SABS 533 PART II TYPE 4
JP | 20-110 (OD) | ELONG. MOULD. PN10 FOR BUTT & ELECTROF. WELDING | HDPE SABS 533 PART II TYPE 4
JP | 20-160 (OD) | MOULDED PN10 FOR BUTT WELDING | HDPE SABS 533 PART II TYPE 4
JP | 160-355 (OD) | MOULDED PN6 FOR BUTT WELDING | HDPE SABS 533 PART II TYPE 4
JP | 20-110 (OD) | ELECTRIC SOCKET (ELECTROFUSION COUPLER) PN10 | HDPE SABS 533 PART II TYPE 4
K3 | 63-400 | EQUAL TEE PLAIN STUB ENDS WITH GALVANISED CS BACKING RING FLANGES TO SANS 1123 | HDPE PE100 PN25 | JAA00045314
K3 | 63-400 | 45° & 60° EQUAL LATERAL, PLAIN STUB ENDS WITH GALVANISED CS BACKING RINGS | HDPE PE100 PN25 | JAA00045314
K3 | 63-400 | CONCENTRIC & ECCENTRIC REDUCER PLAIN ENDS | HDPE PE100 PN25 | JAA00045314
K3 | 63-400 | 90° & 45° 3D BEND, PLAIN STUB ENDS, WITH GALV CS BACKING RING FLANGES | HDPE PE 80, PN 16 (SEAMLESS) | JAA00045314
K3 | 110-280 | 90° & 45° 2D BEND, PLAIN STUB ENDS, WITH GALV CS BACKING RING FLANGES | HDPE PE 80, PN 16 (SEAMLESS) | JAA00045314
K3 | 315-400 | 90° & 45° 1.5D BEND, PLAIN STUB ENDS, WITH GALV CS BACKING RING FLANGES | HDPE PE 80, PN 16 (SEAMLESS) | JAA00045314
K3 | 110-400 | 90° & 45° 5D BEND, PLAIN STUB ENDS, WITH GALV CS BACKING RING FLANGES | HDPE PE 80, PN 16 (SEAMLESS) | JAA00045314
KA1 | 110-280 | HDPE, STUB ENDS, MOULDED TYPE OR FABRICATION FROM PIPE TO STD DRAWING JAA00045314 SHEETS 3,4,5,8 & 9 | MANUFACTURER'S STD | JAA00045314
KA2 | 110-280 | HDPE, STUB ENDS, MOULDED TYPE OR FABRICATION FROM PIPE TO STD DRAWING JAA00045314 SHEETS 3,4,5,8 & 9 | MANUFACTURER'S STD | JAA00045314
KA3 | 110-280 | HDPE, STUB ENDS (SEE NOTES 3 & 4) |  | JAA00045314
M2 | 50-150 | TO STANDARD DRAWING JAA00045303 SHEETS 7,8,11 TO 19 | SABS 62 MED WT SCARFED | JAA00045303
M2 | 200-700 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
MD | 50-150 | C.S. FF 3D FLANGED BEND, RUBBER LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | BEND - SABS 62 MEDIUM, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 200-600 | CS FF 2D 5 SEG. FLANGED BEND, R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | BEND - SABS 719 GR B 6mm WALL, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 50-150 | CS FF FLG'D SHORT EQUAL TEE R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | TEE - FROM SABS 62 MEDIUM, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 20-600 | CS FF FLG'D SHORT EQUAL TEE R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | TEE - FROM SABS 719 GR B 6mm WALL, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 50-150 | CS FF FLG'D UNEQUAL TEE R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | TEE - FROM SABS 62 MEDIUM, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 200-600 | CS FF FLG'D UNEQUAL TEE R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | TEE - FROM SABS 719 GR B 6mm WALL, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 50-150 | CS FF FLG'D EQUAL LATERAL, R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | LATERAL - FROM SABS 62 MEDIUM, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 200-600 | CS FF FLG'D EQUAL LATERAL, R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | LATERAL - FROM SABS 719 GR B 6mm WALL, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 50-150 | CS FF FLG'D UNEQUAL LATERAL, R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | LATERAL - FROM SABS 62 MEDIUM, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MD | 200-600 | CS FF FLG'D UNEQUAL LATERAL, R.LINED 6mm THICK C/W TWO SLIP-ON FLG'S TO ANSI B16.5 CLASS 150# | LATERAL - FROM SABS 719 GR B 6mm WALL, R.LINING - BUTYL R. TYPE 2 GR. B CL.50, FLG'S - ASTM A105 | IAA00045303
MF | 50-150 | CAP BW SCHEDULE 40 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 200-300 | CAP BW SCHEDULE 20 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 350-600 | CAP BW SCHEDULE 10 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 50-150 | BW LR (1.5D) ELBOW SCHED 40 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 200-300 | BW LR (1.5D) ELBOW SCHED 20 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 350-600 | BW LR (1.5D) ELBOW SCHED 10 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 50-150 | REDUCER CONCENTRIC/ECCENTRIC BW SCHED 40 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 200-300 | REDUCER CONCENTRIC/ECCENTRIC BW SCHED 20 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 350-600 | REDUCER CONCENTRIC/ECCENTRIC BW SCHED 10 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 50-150 | EQUAL TEE BW SCHED 40 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 200-300 | EQUAL TEE BW SCHED 20 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 350-600 | EQUAL TEE BW SCHED 10 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 50-150 | REDUCING TEE BW SCHED 40 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 200-300 | REDUCING TEE BW SCHED 20 DIMS TO ASME B16.9 | ASTM A234 WPB
MF | 350-600 | REDUCING TEE BW SCHED 10 DIMS TO ASME B16.9 | ASTM A234 WPB
R3 | 50-150 | TO STANDARD DRAWING JAA00045303 SHEETS 7, 8, 11 TO 19 | SABS 62 MED WT SCARFED | JAA00045303
R3 | 200-600 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
R5 | 50-150 | TO STANDARD DRAWING JAA00045505 SHEETS 7,8,11 TO 15 | SABS 52 MED WT SCARFED | JAA00045505
R5 | 200-400 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
R5 | 450 & 500 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 8 AND 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
R6 | 65-150 | CS STD WT, BW TO STD DRG JAA00045303 SHEETS 5 TO 20 (FOR LINING SEE NOTE 4) | BS 1640 GRD WPB | JAA00045303
R6 | 200-700 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 (FOR LINING SEE NOTE 4) | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
R7 | 80-150 | TO STANDARD DRAWING JAA00045303 SHEETS 7, 8, 11 TO 19 | SABS 62 HVY WT SCARFED | JAA00045303
R7 | 200-400 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
R7 | 450 & 500 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 8 & 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
T2 | 20-50 | TO STD DRG JAA00045305 SHEETS 4 & 5 | BS 1640 GRD WPB SCH 40 | JAA00045305
V5 | 65&UNDER | WS, SCRD TO STD DRG JAA00045310 SHEETS 1 TO 12 | BS 1740 | JAA00045310
V5 | 80-150 | CS, HVY WT, BW, TO STD DRG JAA00045304 SHEETS 1 & 2 | BS 1640 GRD WPB | JAA00045304
V5 | 200 & 250 | TO STD DRG JAA00045300 SHTS 4 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 6mm WALL | JAA00045300/301
V5 | 300 & 350 | TO STD DRG JAA00045300 SHTS 4 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 8mm WALL | JAA00045300/301
V5 | 400 & 450 | TO STD DRG JAA00045300 SHTS 4 TO 8 & JAA00045301 SHT 9 | SABS 719 GRD "B", CS 10mm WALL | JAA00045300/301
R8 | 80-150 | TO STANDARD DRAWING JAA00045303 SHEETS 7, 8, 11 TO 19 | SABS 62 HVY WT SCARFED | JAA00045303
R8 | 200-400 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
R8 | 450 & 500 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 8 & 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
R9 | 80-150 | TO STANDARD DRAWING JAA00045303 SHEETS 7, 8, 11 TO 19 | SABS 62 HVY WT SCARFED | JAA00045303
R9 | 200-400 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 10 | SABS 719 GRD "B", CS 6mm WALL | JAA00045301
R9 | 450 & 500 | TO STANDARD DRAWING JAA00045301 SHEETS 5 TO 8 & 10 | SABS 719 GRD "B", CS 8mm WALL | JAA00045301
V2a | 50 | CS STD WT, BW TO STD DRG JAA00045304 SHEETS 1 & 2 | BS 1640 GRD WPB | JAA00045304
A3 | ALL | NOTES ONLY - NO FITTINGS LISTED (see sheet 1 for pipe details)
G3 | ALL | NOTES ONLY - PIPES & FITTINGS TO BE GALVANISED TO AGS 030
N2 | ALL | NOTES ONLY - ALL PIPES & FITTINGS TO BE INTERNALLY LINED WITH NITRILE RUBBER
N4 | ALL | NOTES ONLY - ALL PIPES & FITTINGS TO BE INTERNALLY LINED WITH NITRILE RUBBER
R10 | ALL | BENDS DETAIL ONLY - MINIMUM BEND RADIUS 5D
S2 | ALL | COVER ONLY
X3 | ALL | NO FITTINGS LISTED - QUICK RELEASE CLAMP JOINTS ONLY
JF | ALL | PVC FITTINGS - SEE SHEET 1 FOR DETAILS
JF2 | ALL | PVC FITTINGS - HOLD FOR HOSE FITTINGS AND CODES
JG | ALL | SMALL BORE / INSTRUMENT - NO STANDARD FITTINGS LISTED
JQ1 | ALL | GRP FITTINGS - DIMENSIONAL TABLES ONLY (see notes)
JR | ALL | GRP FITTINGS - DIMENSIONAL TABLES ONLY (see notes)