## Joints
Spec | Size Range | Joint Type | Description | Material/Type | Drawing Ref
A2 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
A4 | 15-40 | MECH. JOINTS | PLATE FLG., SABS 1123-1000/3 FF | SABS 1431-300 WA
A4 | 50-300 | MECH. JOINTS | PLATE FLG., SABS 1123-1000/3 FF | SABS 1431-300 WA
A4 | 15-300 | MECH. JOINTS | BLANK FLANGE, SABS 1123-1000/8 FF | SABS 1431-300 WA
BA | 8-40 | MECH. JOINTS | UNION SCRD TO ISO R7, BRONZE SEAT, DIMS TO BS 1740 (FIG 18) | BS 1387 | JAA00045310
BA | 50-500 | MECH. JOINTS | SLIP-ON FF CLASS 150#, BORE SABS 62719, DIMS TO ANSI B16.5 | ASTM A105
BA | 15-40 | MECH. JOINTS | SCREWED RF CLASS 150# DIMS TO ANSI B16.5 | ASTM A105
BA | 50-500 | MECH. JOINTS | SLIP ON RF CLASS 150#, BORE SABS 62719, DIMS TO ANSI B16.5 | ASTM A105
BA | 15-500 | MECH. JOINTS | BLIND FLANGE RF CLASS 150# DIMS TO ANSI B16.5 | ASTM A105
BA | 15-500 | MECH. JOINTS | BLIND FLANGE FF CLASS 150# DIMS TO ANSI B16.5 | ASTM A105
BB | 15-40 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, SABS 62 BORE, DIMS TO ANSI B16.5 | ASTM A105
BB | 50-200 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, SABS 62719 BORE, DIMS TO ANSI B16.5 | ASTM A105
BB | 15-200 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMS TO ANSI B16.5 | ASTM A105
BC | 15-50 | MECH. JOINTS | FLG WN CLASS 150# RF, SCHED 80 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BC | 80-200 | MECH. JOINTS | FLG WN CLASS 150# RF, SCHED 40 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BC | 15-200 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMS TO ANSI B16.5 | ASTM A105
BD | 15-40 | MECH. JOINTS | FLG WN CLASS 150# RF, SCHED 80 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BD | 50-300 | MECH. JOINTS | FLG WN CLASS 150# RF, SCHED 40 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BD | 15-300 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMS TO ANSI B16.5 | ASTM A105
A5 | 8-32 | PERM. JOINTS | WROUGHT STEEL COUPLING SCRD TO SABS 1109, DIM.S TO SABS 509 | ASTM A106 B
A5 | 8-32 | PERM. JOINTS | HALF COUPLING SCRD TO SABS 1109, CL. 3000 DIMS TO SABS 509 | ASTM A105
BE | 15-40 | PERM. JOINTS | SOCKET WELD FULL CPLG 3000# DIMENSIONS TO ASME B16.11 | ASTM A105
BE | 15-40 | PERM. JOINTS | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ASME B16.11 | ASTM A105
BF | 15-40 | MECH. JOINTS | FLG RF SOCKET WELD 150#, SCHED 80 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BF | 50-200 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, SCHED 40 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BF | 15-200 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMS TO ANSI B16.5 | ASTM A105
BF | 8-15 | PERM. JOINTS | SOCKET WELD UNION CLASS 3000# DIMS TO ANSI B16.11 | ASTM A105
BH | 15-40 | MECH. JOINTS | FLG RF SOCKET WELD CLASS 150#, SCHED 80 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182 F11
BH | 50-150 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, SCHED 40 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182 F11
BH | 200-300 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, SCHED 20 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182 F11
BH | 350-500 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, SCHED 10 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182 F11
BH | 15-40 | MECH. JOINTS | FLG RF SOCKET WELD CLASS 300#, SCHED 80 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182 F11
BH | 50-150 | MECH. JOINTS | FLG RF SLIP-ON CLASS 300#, SCHED 40 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182 F11
BH | 15-500 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMENSIONS TO ANSI B16.5 | ASTM A182 F11
BI | 15-40 | MECH. JOINTS | FLG RF SOCKET WELD CLASS 150#, SCHED 40 BORE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BI | 50-150 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, BORE TO FIT OD PIPE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BI | 200-500 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, BORE TO FIT OD PIPE, DIMENSIONS TO ANSI B16.5 | ASTM A105
BI | 15-500 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMENSIONS TO ANSI B16.5 | ASTM A105
BJ | 15-40 | MECH. JOINTS | TO BS 1740: 1965, ISO R7
BJ | 50-800 | MECH. JOINTS | TO ANSI B16.5 CLASS 150# FF SLIP ON FLANGES FOR WELDING
C4 | 200-450 | ALL JOINTS | CS, FLANGES TO STD DRG JAA00045204 SHT 2 | BS 4360 GRD 43A | JAA00045204
C6 | 200-450 | ALL JOINTS | CS, FLANGES TO STD DRG JAA00045204 SHT 4 | BS 4360 GRD 43A | JAA00045204
C8 | 200-450 | ALL JOINTS | CS, FLANGES TO STD DRG JAA00045204 SHT 6 | BS 4360 GRD 43A | JAA00045204
CF4 | 200-250 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CF4 | 300-400 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 64/3 RF | SABS 1431 GRADE 300W
CL4 | 200-250 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CL4 | 300-400 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 64/3 RF | SABS 1431 GRADE 300W
DC3 | ALL SIZES | MECH. JOINTS | CS, FLANGES TO SABS 1123 T1600/3 FF | SELECT FROM SABS 1123
DC3 | 15-50 | PERM. JOINTS | SW COUPLING | BS 3799 GRD WPB
DC3 | 65-450 | PERM. JOINTS | BW
E4 | 200-500 | PERM. JOINTS | CS, SLEEVES (SEE NOTE 6) | SABS 719 GRADE "B" OR EQUIVALENT | JAA00045313
E4 | 200-250 | MECH. JOINTS | CS, FLANGES TO BS 4504 T64/3 | SABS 1431 GRADE 300 WA
E4 | 300-400 | MECH. JOINTS | CS, FLANGES TO BS 4504 T40/3 | SABS 1431 GRADE 300 WA
E4 | 500 | MECH. JOINTS | CS, FLANGES TO BS 4504 T25/3 | SABS 1431 GRADE 300 WA
E5 | 200-500 | PERM. JOINTS | CS, SLEEVES (SEE NOTE 6) | SABS 719 GRADE "B" OR EQUIVALENT | JAA00045313
E5 | 200-250 | MECH. JOINTS | CS, FLANGES TO BS 4504 T100/3 | SABS 1431 GRADE 300 WA
E5 | 250-400 | MECH. JOINTS | CS, FLANGES TO BS 4504 T64/3 | SABS 1431 GRADE 300 WA
E5 | 500 | MECH. JOINTS | CS, FLANGES TO BS 4504 T40/3 | SABS 1431 GRADE 300 WA
E9 | 200-500 | PERM. JOINTS | CS, SLEEVES (SEE NOTE 6) | SABS 719 GRADE "B" OR EQUIVALENT | JAA00045313
E9 | 250-300 | MECH. JOINTS | CS, FLANGES TO BS 4504 T160/3 | SABS 1431 GRADE 300 WA
E9 | 350-500 | MECH. JOINTS | CS, FLANGES TO BS 4504 T100/3 | SABS 1431 GRADE 300 WA
EB | 15-40 | MECH. JOINTS | FLG RF WELD NECK CLASS 150, SHED 40S BORE, DIMENSIONS TO ASME B16.5 | ASTM A182-F316 L
EB | 50-250 | MECH. JOINTS | FLG RF WELD NECK CLASS 150, SHED 10S BORE, DIMENSIONS TO ASME B16.5 | ASTM A182-F316 L
EB | 50-350 | MECH. JOINTS | FLG RF WELD NECK CLASS 150, SHED 10S BORE, DIMENSIONS TO ASME B16.5 | ASTM A182-F316 L
EB | 15-300 | MECH. JOINTS | BLIND FLANGE RF CLASS 150, DIMENSIONS TO ASME B16.5 | ASTM A182-F316 L
EB | 15-40 | PERM. JOINTS | SOCKET WELD HALF CPLG CL 3000, DIMENSIONS TO ASME B16.11 | ASTM A182-F316 L
EB | 15-40 | PERM. JOINTS | SCRD TO ISO R7 HALF CPLG CL 3000, DIMENSIONS TO ASME B16.11 | ASTM A182-F316 L
EC | 15-40 | MECH. JOINTS | SOCKET WELD RF FLG CLASS 300#, SCHED 40S BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182-F316 L
EC | 50-300 | MECH. JOINTS | FLG RF WELD NECK CLASS 300#, SCHED 10S BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182-F316 L
EC | 15-300 | MECH. JOINTS | BLIND FLANGE RF CLASS 300#, DIMS TO ANSI B16.5 | ASTM A182-F316 L
EC | 15-40 | PERM. JOINTS | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316 L
EC | 15-40 | PERM. JOINTS | SCRD TO ISO R7 HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316 L
ED | 15-40 | MECH. JOINTS | FLG SLIP-ON CLASS 150# RF, SCHED 40S BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182-F316L
ED | 50-100 | MECH. JOINTS | FLG SLIP-ON CLASS 150# RF, SCHED 10S BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182-F316L
ED | 150-600 | MECH. JOINTS | FLG LAPPED CLASS 150#, SCHED 5S BORE MS ECTFE COATED, DIMS TO ANSI B16.5 | ASTM A105, ECTFE COATED
ED | 15-600 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMENSIONS TO ANSI B16.5 | ASTM A182-F316L
ED | 15-40 | PERM. JOINTS | SCRD TO ISO R7 HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
ED | 15-40 | PERM. JOINTS | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
EF | 15-40 | MECH. JOINTS | FLG RF WELD NECK CLASS 150#, SCHED 40S BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182-F316L
EF | 50-300 | MECH. JOINTS | FLG RF WELD NECK CLASS 150#, SCHED 10S BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182-F316L
EF | 15-300 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMENSIONS TO ANSI B16.5 | ASTM A182-F316L
EF | 15-40 | PERM. JOINTS | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
EF | 15-40 | PERM. JOINTS | SCRD TO ISO R7 HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F316L
EH | 15-40 | MECH. JOINTS | FLG RF SOCKET WELD CLASS 150#, 304 SS, SCHED 40S BORE, DIMS TO ANSI B16.5 | ASTM A182-F304
EH | 50-300 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, 304 SS, SCHED 10S BORE, DIMS TO ANSI B16.5 | ASTM A182-F304
EH | 350-500 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, 304 SS, SCHED 5S BORE, DIMS TO ANSI B16.5 | ASTM A182-F304
EH | 15-40 | MECH. JOINTS | FLG RF SOCKET WELD CLASS 300#, 304 SS, SCHED 40S BORE, DIMS TO ANSI B16.5 | ASTM A182-F304
EH | 50-300 | MECH. JOINTS | FLG RF SLIP-ON CLASS 300#, 304 SS, SCHED 10S BORE, DIMS TO ANSI B16.5 | ASTM A182-F304
EH | 15-500 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMENSIONS TO ANSI B16.5 | ASTM A182-F304
EJ | 100-1600 | MECH. JOINTS | FABRICATED DUCT SPOOL PIECE MAX 6000mm LONG WITH WELDED PLATE FLANGES | ASTM A240 Grade 304 PLATE
EJ | 50-300 | MECH. JOINTS | SCHEDULE 10S, SEAMLESS, DIMENSIONS TO ASME B36.19 | ASTM A312 GR TP 304
EJ | 350-500 | MECH. JOINTS | SCHEDULE 5S, ELECTRIC-FUSION-WELDED, BEVELLED ENDS TO ASTM A358 CLASS 2 | ASTM A240 TYPE 304
EK | 100-1600 | MECH. JOINTS | FABRICATED DUCT SPOOL PIECE MAX 6000mm LONG WITH WELDED PLATE FLANGES | Hastelloy C-276
EK | 50-300 | MECH. JOINTS | SCHEDULE 10S, SEAMLESS, DIMENSIONS TO ASME B36.19 | Hastelloy C-276
EK | 350-500 | MECH. JOINTS | SCHEDULE 5S, ELECTRIC-FUSION-WELDED, BEVELLED ENDS TO ASTM A358 CLASS 2 | Hastelloy C-276
F2 | 80-600 | ALL JOINTS | VIKING-JOHNSON COUPLINGS (SEE NOTE 5) | BS 4360 GRADE 43A
FC3 | ALL SIZES | MECH. JOINTS SPEC AR | CS, FLANGES TO SABS 1123 T1600/3 RF | SELECT FROM SABS 1123
FC3 | ALL SIZES | MECH. JOINTS SPEC SC | CS, FLANGES TO SABS 1123 T1600/3 FF | SELECT FROM SABS 1123
FC3 | 15-50 | PERM. JOINTS | SW COUPLING | BS 3799 GRD WPB
FC3 | 65 & OVER | PERM. JOINTS | BW
G2 | 50&UNDER | MECH. JOINTS | MI, UNIONS, BRONZE TAPER SEAT, GALVD SCRD TO BSP | SABS 509
G2 | 65 | MECH. JOINTS | MI, UNIONS, BRONZE TAPER SEAT, GALVD SCRD TO BSP | BS 143
G2 | 65&UNDER | MECH. JOINTS | GALV. FLANGES TO SABS 1123 T1000/4 FF, ONLY FOR IN-LINE FLANGED ITEMS | SELECT FROM SABS 1123
G2 | 65&UNDER | PERM. JOINTS | SCRD & SOCKETED TO BSP
G2 | 80-700 | PERM. JOINTS | CS, FLANGES, SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
G2A | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
G4 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T2500/3 FF | SELECT FROM SABS 1123
G5 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T4000/3 FF | SELECT FROM SABS 1123
G6 | 50& UNDER | MECH. JOINTS | CS FLANGES, SCR'D ANSI B16.5 CLASS 600 RF, GALV'D | ASTM A105
G6 | 50& UNDER | PERM. JOINTS | FS, CLASS 3000, SCR'D TO ANSI B2.1, GALVANIZED | ANSI B16.11
GA | 50-150 | MECH. JOINTS | SLIP-ON FF CLASS 150#, DIMS TO ANSI B16.5 | ASTM A105
GA | 15-150 | MECH. JOINTS | SCREWED FF CLASS 150# DIMS TO ANSI B16.5 | ASTM A105
GA | 15-150 | MECH. JOINTS | SCREWED FF CLASS 150# DIMS TO ANSI B16.5 | ASTM A105
GA | 15-150 | MECH. JOINTS | LONG SCREW CW SOCKET AND M.C.I. BACKNUTS TAPER THREAD TO ISO R7 | SABS 62
GA | 15-80 | MECH. JOINTS | SCRD TO ISO R7, UNION TAPER SEAT, DIMS TO SABS 509 | SABS 509-1975
GA | 15-150 | PERM. JOINTS | FORGED STEEL COUPLING SCRD TO ISO R7, DIMS TO ANSI B16.11 | ASTM A105 HOT DIP GALV'S TO SABS 763
H2 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
HA | 15-150 | ALL JOINTS | GLASS PIPE WITH BUTTRESS ENDS TYPE 'A' (CORNING 1992-PAGE 1.7/E) | BOROSILICATE GLASS - ISO 3585 / BS 2598 PART 1
I2 | 15-50 | MECH. JOINTS | LAP JOINT FLANGE, RF, DIMS TO ANSI B16.5 CLASS 150# | ASTM A105
I2 | 80-900 | MECH. JOINTS | SOLID GREY OR DUCTILE IRON FLANGE, DIM TO ANSI/AWWA C115/A21.15, TABLE 2 CLASS 250#, THREADED TO ASME/ANSI B1.20.1-TAPER THREAD | ASTM A536, Gr. 70-50-5
I2 | 80-900 | MECH. JOINTS | INTEGRALLY CAST DUCTILE IRON FLANGES, DIMS TO ANSI/AWWA C110/A21.10-1993 TABLE 10.14-FIGURE 10.14 | ASTM A536, Gr. 70-50-5
I2 | 15-50 | MECH. JOINTS | USE END CAPS
I2 | 80-600 | MECH. JOINTS | DUCTILE IRON BLIND FLANGE, DIMS TO ANSI B16.42-1987, TABLE 4 CLASS 150# | ASTM A536, Gr. 70-50-5
I2 | 15-50 | PERM. JOINTS | SOCKET WELD FULL CPLG 3000# DIMENSIONS TO ANSI B16.11 | ALLOY 20 / ASTM B 464
JA | 20-110 (OD) | PERM. JOINTS | MOULDED PN10 FOR SOCKET FUSION DIMS DRG JAAXXXXXXX X REF: GF 27.15.01 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 125-225 (OD) | PERM. JOINTS | MOULDED PN10 FOR BUTT WELDING DIMS DRG JAAXXXXXXX X REF: AGRU 60 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 140-225 (OD) | PERM. JOINTS | MOULDED PN10 FOR BUTT WELDING DIMS DRG JAAXXXXXXX X REF: GF 27.01.09 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JA | 250-400 (OD) | PERM. JOINTS | MOULDED PN10 FOR BUTT WELDING DIMS DRG JAAXXXXXXX X REF: AGRU 01 | POLYPROPYLENE (CO-POLYMER) SABS 1315
JB | 20-400 (OD) | MECH. JOINTS | MS BACKING RING (BACKING FLG) ECTFE COATED DRILLED TO ANSI B16.5 CLASS 150 DIMS DRG JAA00045203 1 | ASTM A234 WPB ECTFE COATED
JB | 15-100 (OD) | MECH. JOINTS | MS ECTFE COATED RF CLASS 150# DIMS TO ANSI B16.5 | ASTM A105 ECTFE COATED
JB | 20-50 (OD) | MECH. JOINTS | STUB FLG (FLG ADAPTOR) MOULDED PN16 FOR SOCKET FUSION FLAT FACE DIMS TO DIN 8063/5 REF: GF 35.80.01 | PVDF - POLYVINYLIDENE FLUORIDE
JB | 63-110 (OD) | MECH. JOINTS | STUB FLG (FLG ADAPTOR) MOULDED PN16 FOR SOCKET FUSION SERRATED FACE DIMS TO DIN 8063/5 REF: GF 35.79.01 | PVDF - POLYVINYLIDENE FLUORIDE
JB | 20-110 (OD) | PERM. JOINTS | MOULDED PN16 FOR SOCKET FUSION DIMS TO DIN 8063/5 REF: GF 35.10.01 | PVDF - POLYVINYLIDENE FLUORIDE
JC | 20-110 (OD) | MECH. JOINTS | MS BACKING RING (BACKING FLG) ECTFE COATED DRILLED TO ANSI B16.5 CLASS 150 DIMS DRG JAA00045203 1 | ASTM A234 WPB ECTFE COATED
JC | 15-100 (OD) | MECH. JOINTS | MS ECTFE COATED RF CLASS 150# DIMS TO ANSI B16.5 | ASTM A105 ECTFE COATED
JC | 20-110 (OD) | MECH. JOINTS | STUB FLG (FLG ADAPTOR) MOULDED PN12.5 FOR SOLVENT CEMENT WELDING. SERRATED FACE. DIMS TO ISO 727 & DIN 8063/5 | ABS
JC | 20-110 (OD) | PERM. JOINTS | MOULDED PN12.5 FOR SOLVENT CEMENT WELDING. DIMS TO ISO727&DIN 8063/5 | ABS
JD | 25-1600 | PERM. JOINTS | RTRP BUTT AND OVERWRAP 90° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JF | 20-400 (OD) | MECH. JOINTS | MS BACKING RING (BACKING FLG) ECTFE COATED DRILLED TO ANSI B16.5 CLASS 150 DIMS DRG JAA00045203 1 | ASTM A234 WPB ECTFE COATED
JF | 15-400 (OD) | MECH. JOINTS | MS ECTFE COATED RF CLASS 150# DIMS TO ANSI B16.5 | ASTM A105 ECTFE COATED
JF | 20-50 (OD) | MECH. JOINTS | STUB FLG (FLG ADAPTOR) MOULDED PN10 FOR SOCKET FLAT FACE REF: GF 21.80.01 | UPVC SABS 966
JF | 63-225 (OD) | MECH. JOINTS | STUB FLG (FLG ADAPTOR) MOULDED PN10 FOR SOLVENT SOCKET SERRATED FACE REF: GF 21.79.01 | UPVC SABS 966
JF2 | 20-160 (OD) | MECH. JOINTS | MS GALVANIZED BACKING RING, DIM AND DRILLING TO SABS 1123 PN 1600 | BS 4360 Grade 43A PLATE OR EQUIVALENT
JF2 | 15-150 | MECH. JOINTS | MS BLIND FLANGE WITH 3mm THK PTFE BACKED EPDM SHEET (FULL FACE). DIMENSIONS AND DRILLING TO SABS 1123 PN 1600 | BS 4360 Grade 43A PLATE OR EQUIVALENT
JF2 | 20-160 (OD) | MECH. JOINTS | STUB FLG (FLG ADAPTOR) MOULDED PN16 FOR SOLVENT WELDING SOCKET, SERRATED FACE. REF: +GF+ 21 79 01 | CPVC - CHLORINATED POLYVINYL CHLORIDE
JH | 25-1600 | MECH. JOINTS | FULL FACE FIBREGLASS CONTACT MOULDED FROM CHOPPED STRAND MAT AND WOVEN ROVINGS IMPREGNATED THERMOSETTING RESIN WITH INTEGRAL CORROSION BARRIER LINER OF 2mm THK | RTRP | IAA00045376
JH | 25-600 | MECH. JOINTS | RAISED FACE STUB FIBREGLASS MOULDED FROM C.S.M AND W.R. IMPREGNATED THERMOSETTING RESIN WITH INTEGRAL CORROSION BARRIER LINER OF 2mm THICK | STUB: RTRP | IAA00045376
JH | 25-100 | MECH. JOINTS | S.M.C. (SHEET MOULDED COMPOUND) BACKING RING AS PER DRG No: IAA00045376 3/5 | BACKING RING: SMC | IAA00045376
JH | 150-600 | MECH. JOINTS | MS ECTFE COATED BACKING RING AS PER DRG No: IAA00045376 3/5 | BACKING RING: ASTM A105 | IAA00045376
JH | 25-1600 | MECH. JOINTS | FULL FACE FIBREGLASS CONTACT MOULDED FROM CHOPPED STRAND MAT AND WOVEN ROVINGS IMPREGNATED THERMOSETTING RESIN WITH INTEGRAL CORROSION BARRIER LINER OF 2mm THK | FLANGE: RTRP | IAA00045376
JM | 20-160 (OD) | PERM. JOINTS | (2.5 D) MOULDED PN6 FOR SOLVENT SOCKET DIMS ISO 264 REF: GF 21.00.01 | UPVC SABS 966
JN | 20-160 (OD) | PERM. JOINTS | (2D) MOULDED PN10 FOR SOLVENT SOCKET DIMS ISO 264 REF: GF 21.00.01 | UPVC SABS 966
JN | 225 (OD) | PERM. JOINTS | (0.75 D) MOULDED PN10 FOR SOLVENT SOCKET DIMS ISO 264 REF: GF 21.01.01 | UPVC SABS 966
JN | 20-160 (OD) | PERM. JOINTS | MOULDED PN10 FOR SOLVENT SOCKET DIMS ISO 264 REF: GF 21.91.01 | UPVC SABS 966
JO | 25-250 | PERM. JOINTS | RTRP BUTT AND OVERWRAP 90° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JP | 20-110 (OD) | PERM. JOINTS | ELONGATED MOULDED PN10 FOR BUTT & ELECTROFUSION WELDING REF: AGRU II | HDPE SABS 533 PART II TYPE 4
JP | 125-400 (OD) | PERM. JOINTS | MOULDED PN6 FOR BUTT WELDING REF: GF 33.10.08/AGRU 01 | HDPE SABS 533 PART II TYPE 4
JP | 20-110 (OD) | PERM. JOINTS | ELECTRIC SOCKET (ELECTROFUSION COUPLER) PN10 REF: GF 33.91.06/AGRU 73 | HDPE SABS 533 PART II TYPE 4
JQ | 25-1600 | PERM. JOINTS | RTRP BUTT AND OVERWRAP 90° BEND CONTACT MOULDED | VINYL ESTER DERAKANE 411-45 | IAA00045376
JQ1 | ALL SIZES | ALL JOINTS | GRP PIPEWORK - SEE NOTE 7 FOR DETAILS | VINYL ESTER CORREZYN VE8300
JR | ALL SIZES | ALL JOINTS | GRP PIPEWORK - SEE NOTE 7 FOR DETAILS | CORREZYN VE 8300-EX-45
K1 | 63-500 | ALL JOINTS FLANGED | HDPE STUB FLANGES WITH GALVANISED CS BACKING RING FLANGE TO SANS 1123 1000 kPa TO STD DRG JAA0045314 SHTS 10 &11 | HDPE PE80, PN8 TO MACHINED STUBS DIN 16963: PART 4 | JAA0045314
K1 | 63-500 | BLIND FLANGE | HDPE STUB FLANGES WITH GALVANISED CS BACKING RING & BLIND FLANGE TO SANS 1123 1000 kPa TO STD DRG JAA 0045314 SHTS 10 &11 | HDPE PE80, PN8 MACHINED STUBS DIN 16963: PART 4 | JAA0045314
K2 | 63-500 | ALL JOINTS FLANGED | HDPE STUB FLANGES WITH GALVANISED CS BACKING RING FLANGE TO SANS 1123 1000 kPa TO STD DRG JAA0045314 SHTS 10 &11 | HDPE PE80, PN12.5 TO MACHINED STUBS DIN 16963: PART 4 | JAA0045314
K2 | 63-500 | BLIND FLANGE | HDPE STUB FLANGES WITH GALVANISED CS BACKING RING & BLIND FLANGE TO SANS 1123 1000 kPa TO STD DRG JAA 0045314 SHTS 10 &11 | HDPE PE80, PN12.5 MACHINED STUBS DIN 16963: PART 4 | JAA0045314
K3 | 63-400 | ALL JOINTS FLANGED | HDPE STUB FLANGES WITH GALVANISED CS BACKING RING FLANGE TO SANS 1123 1600 kPa TO STD DRG JAA0045314 SHTS 10 &11 | HDPE PE80, PN16 TO MACHINED STUBS DIN 16963: PART 4 | JAA0045314
K3 | 63-400 | BLIND FLANGE | HDPE STUB FLANGES WITH GALVANISED CS BACKING RING & BLIND FLANGE TO SANS 1123 1600 kPa TO STD DRG JAA 0045314 SHTS 10 &11 | HDPE PE80, PN16 MACHINED STUBS DIN 16963: PART 4 | JAA0045314
KA1 | 110-280 | PERM. JOINTS | HDPE STUB AND CLAMPS TO STD DRAWING No JAA00045314 SHEET 12 | MANUFACTURER'S STD | JAA00045314
KA1 | 110-280 | MECH JOINTS | HDPE STUB FLANGES WITH CS BACKING RINGS TO STD DRG No JAA00045314 SHEETS 10 & 11 | CLASS 6 STUB WITH SABS 1123 T/1000 BACKING RING | JAA00045314
M2 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
MA | 25-150 | ALL JOINTS | PIPE, SEAMLESS, SCHED 40, TO ASME B36.10M WITH FLARED ENDS C/W TWO LOOSE BACKING RINGS DRILLED TO ASME B16.5 CLASS 150 POLYPROPYLENE LINED PASTE MOULDED TO VENDOR SPECIFICATION | POLYPROPYLENE LINED
MB | 25-150 | MECH. JOINTS | C.S. SEAMLESS, SCHED 40, RF SPOOL PIECE 100 OR 125mm LONG PVDF LINED 2.7mm THICK C/W ONE FLANGE WELDED AND THE OTHER LOOSE. WELDED FLG TO ANSI B16.5 FF CLASS 150# | PIPE - ASTM A 106 Gr B / PVDF - ASTM D 638 BLUE / FLGS - ASTM A105 | IAA00045300
MB | 25-150 | MECH. JOINTS | C.S. SEAMLESS, SCHED 40 RF. SPOOL PIECE 150-6000mm LONG PVDF LINED 2.7mm THICK C/W TWO LOOSE FLANGES. FLANGES LAPPED TO ANSI B16.5 CLASS 150# | PIPE - ASTM A 106 Gr B / PVDF - ASTM D 638 BLUE / FLGS - ASTM A105 | IAA00045300
MB | 25-150 | MECH. JOINTS | BLIND FLANGE RF TO ANSI B16.5 CLASS 150# WITH FULL FACE PTFE FACING 3mm THICK | ASTM A105
MC | 25-400 | ALL JOINTS | SEAMLESS, SCHED 40, TO ASME B36.10M WITH FLARED ENDS C/W TWO LOOSE BACKING RINGS DRILLED TO ASME B16.5 CL 150. PTFE LINED PASTE EXTRUDED TO VENDOR SPECIFICATION | PIPE - ASTM A 106 Gr B / BACKING RING - ASTM A105 / LINING - PTFE - ASTM D-1457 TYPE III WHITE
MD | 50-150 | MECH. JOINTS | CS ERW MED WT SCARFED, FF SPOOL PIECE. RUBBER LINED 6mm THICK C/W TWO SLIP-ON FLGS TO ANSI B16.5 CLASS 150#. R. LINING IN ACCORD. WITH SABS 1198 | SPOOL - SABS 62 MEDIUM / R.LINING-BUTYL R. TYPE 2 GR. B CL.50 / FLGS - ASTM A105
MD | 150-600 | MECH. JOINTS | CS ERW 6mm WALL, SCARFED, FF SPOOL PIECE. R.LINED 6mm THICK C/W TWO SLIP-ON FLGS TO ANSI B16.5 CLASS 150#. R. LINING IN ACCORD. WITH SABS 1198 | SPOOL - SABS 719 Gr B 6mm WALL / R.LINING - BUTYL R. TYPE 2 GR. B CL.50 / FLGS - ASTM A105
MF | 50-150 | MECH. JOINTS | FLG SLIP-ON, CLASS 150 RF, SHED 40 BORE, DIMENSIONS TO ASME B16.5 | ASTM A105
MF | 200-300 | MECH. JOINTS | FLG SLIP-ON, CLASS 150 RF, SHED 20 BORE, DIMENSIONS TO ASME B16.5 | ASTM A105
MF | 350-600 | MECH. JOINTS | FLG SLIP-ON, CLASS 150 RF, SHED 10 BORE, DIMENSIONS TO ASME B16.5 | ASTM A105
MF | 50-600 | MECH. JOINTS | BLIND FLANGE RF CLASS 150, DIMENSIONS TO ASME B16.5 | ASTM A105
O1 | 15-40 | MECH. JOINTS | FLANGE WELD NECK CL 150 RFSF SCHED 40S BI | ASTM A182 Gr.F316L
O1 | 50-150 | MECH. JOINTS | FLANGE WELD NECK CL 150 RFSF SCHED 10S BI | ASTM A182 Gr.F316L
O1 | 15-150 | MECH. JOINTS | BLIND FLG. CL 150 RFSF DIMS TO ANSI B16.5 | ASTM A240 Gr. 316L
O1 | 15-40 | PERM. JOINTS | HALF COUPLING SCRD CL 3000 DIMS TO ANSI B16.11 | ASTM A182 Gr.F316L
O1 | 15-40 | PERM. JOINTS | WELDOLET SCHED 40S DIMS TO MSS SP-97 | ASTM A182 Gr.F316L
P2 | ALL SIZES | MECH. JOINTS | SOLVENT WELDED SOCKETS uPVC CLASS 9 | SABS 966
R2 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
R4 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T2500/3 FF | SELECT FROM SABS 1123
A2 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
A5 | 8-32 | PERM. JOINTS | WROUGHT STEEL COUPLING SCRD TO ANSI B2.1, CL. 3000 DIMS TO ANSI B16.11 | ASTM A 106 B
A5 | 8-32 | PERM. JOINTS | HALF COUPLING SCRD TO SABS 1109, CL. 3000 DIMS TO ANSI B16.11 | ASTM A 105
A5 | 8-32 | PERM. JOINTS | M.C.I. SOCKET (COUPLING) SCRD TO SABS 1109 | SABS 509
AA2 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
S3 | 15-300 | MECH. JOINTS | WELDNECK, DIM TO ANSI B16.5, 150#, RF | ASTM A182 Gr. F316L / ASTM A351 Gr. CF3M
S3 | 15-300 | MECH. JOINTS | BLIND, DIM TO ANSI B16.5, 150#, RF | ASTM A182 Gr. F316L / ASTM A351 Gr. CF3M
S3 | ALL SIZES | PERM. JOINTS | BUTT WELD WITH MIN. FLANGES
S3 | 15-40 | PERM. JOINTS | SCREWED ISO R7, 3000#, DIM TO ANSI B16.11/BS 3799 | ASTM A182 Gr. F316L
S3 | 15-40 | PERM. JOINTS | SOCKET WELD, 3000#, DIM TO ANSI B16.11/BS 3799 | ASTM A182 Gr. F316L
AA5 | ALL SIZES | ALL JOINTS | CS FLANGES TO SABS 1123 T4000/3 FF | SELECT FROM SABS 1123
TL2 | 20-50 | ALL JOINTS | CS FLANGES, SABS 1123 TABLE 4000/3 RF, WELDNECK | SABS 1431 GRADE 300W
AF2 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 RF | SABS 1431 GRADE 300W
AF3 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1600/3 RF | SABS 1431 GRADE 300W
AL2 | ALL SIZES | ALL JOINTS | CS FLANGES TO SABS 1123 T1000/3 RF | SABS 1431 GRADE 300W
B4 | 50-150 | ALL JOINTS | CS, FLANGES TO STD DRG JAA00045203 SHT 2 | BS 4360 GRD 43A | JAA00045203
AL3 | ALL SIZES | ALL JOINTS | CS FLANGES TO SABS 1123 T1600/3 RF | SABS 1431 GRADE 300W
BF2 | 50-125 | ALL JOINTS | CS, FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
BF2 | 150-300 | ALL JOINTS | CS, FLANGES TO BS4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
BL2 | 50-125 | ALL JOINTS | CS, FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
BL2 | 150-300 | ALL JOINTS | CS, FLANGES TO BS4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CF5 | 200 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
CF5 | 250-350 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CF5 | 400 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 64/3 RF | SABS 1431 GRADE 300W
CF7 | 250 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
CF7 | 300-400 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CL7 | 250 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
CL7 | 300-400 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
DC5 | All sizes | Mech joints | CS, Flanges to SABS 1123 T4000 F.F | Select from SABS 1123
DC5 | 15-50 | Perm joints | SW Coupling | SABS 52 MED WT scarf
DC5 | 85-450 | Perm joints | BW
BL3 | 125-300 | ALL JOINTS | CS, FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
BL3 | 300 | ALL JOINTS | CS, FLANGES TO BS4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
E2 | 100-250 | PERM. JOINTS | CS, SLEEVES (SEE NOTE 6) | ASTM A106 GRADE "B" OR EQUIVALENT | JAA00045313
E2 | 100-250 | MECH. JOINTS | SEE NOTE 5
E3 | 100-250 | PERM. JOINTS | CS, SLEEVES (SEE NOTE 6) | ASTM A106 GRADE "B" OR EQUIVALENT | JAA00045313
E3 | 100-250 | MECH. JOINTS | SEE NOTE 5
E6 | 200-500 | PERM. JOINTS | CS, SLEEVES (SEE NOTE 6) | SABS 719 GRADE "B" OR EQUIVALENT | JAA00045313
E6 | 200-250 | MECH. JOINTS | CS, FLANGES TO BS 4504 T100/3 | SABS 1431 GRADE 300 WA
E6 | 300-400 | MECH. JOINTS | CS, FLANGES TO BS 4504 T64/3 | SABS 1431 GRADE 300 WA
E6 | 500 | MECH. JOINTS | CS, FLANGES TO BS 4504 T40/3 | SABS 1431 GRADE 300 WA
EA | 15-40 | MECH. JOINTS | FLG RF SLIP ON CLASS 150#, SCHED 40S BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182-F304 L
EA | 50-300 | MECH. JOINTS | FLG RF SLIP-ON CLASS 150#, SCHED 10S BORE, DIMENSIONS TO ANSI B16.5 | ASTM A182-F304 L
EA | 15-300 | MECH. JOINTS | BLIND FLANGE RF CLASS 150#, DIMS TO ANSI B16.5 | ASTM A182-F304 L
EA | 15-40 | PERM. JOINTS | SOCKET WELD HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F304 L
EA | 15-40 | PERM. JOINTS | SCRD TO ISO R7 HALF CPLG 3000# DIMENSIONS TO ANSI B16.11 | ASTM A182-F304 L
G3 | ALL SIZES | ALL JOINTS | PIPES & FITTINGS TO BE GALVANISED TO AGS 030
GL2 | 50&UNDER | MECH. JOINTS | MI, UNIONS, BRONZE TAPER SEAT, GALV. SCR'D TO BSP | SABS 509
GL2 | 65 | MECH. JOINTS | MI, UNIONS, BRONZE TAPER SEAT, GALV. SCR'D TO BSP | BS143
GL2 | 65&UNDER | MECH. JOINTS | GALV. FLANGES TO SABS 1123 T1000/4 FF ONLY FOR IN-LINE FLANGED ITEMS | SABS 1431 GRADE 300W
GL2 | 65&UNDER | PERM. JOINTS | SCR'D & SOCKETED TO BSP
JE | 25-1600 | PERM. JOINTS | GRP BUTT AND OVERWRAP 90° BEND CONTACT MOULDED | QUACORR 1200 F.R. (FURANE) | IAA00045376
KA2 | 110-280 | PERM. JOINTS | HDPE STUB AND CLAMPS TO STD DRAWING No JAA00045314 SHEET 12 | MANUFACTURER'S STD | JAA00045314
KA2 | 110-280 | MECH JOINTS | HDPE STUB FLANGES WITH CS BACKING RINGS TO STD DRG No JAA00045314 SHEETS 10 & 11 | SABS 1123 TABLE 1000 | JAA00045314
KA3 | 110-280 | PERM. JOINTS | HDPE STUB AND CLAMPS TO STD DRAWING No JAA00045314 SHEET 12 | MANUFACTURER'S STD | JAA00045314
KA3 | 110-280 | MECH JOINTS | HDPE STUB FLANGES WITH CS BACKING RINGS TO STD DRG No JAA00045314 SHEETS 10 & 11 | SABS 1123 TABLE 1600 | JAA00045314
N2 | ALL SIZES | ALL JOINTS | ALL PIPES & FITTINGS TO BE INTERNALLY LINED WITH NITRILE RUBBER TO GENERAL SPECIFICATION AGS-017. LINING TO BE 6mm THICK
N4 | ALL SIZES | ALL JOINTS | ALL PIPES & FITTINGS TO BE INTERNALLY LINED WITH NITRILE RUBBER TO GENERAL SPECIFICATION AGS-017. LINING TO BE 8mm THICK
Q2 | 10-50 | ALL JOINTS | POLY AGRO LDPE POLY TYPE 1 Nylon Insert Fittings | POLY AGRO LDPE POLY
R10 | ALL SIZES | ALL JOINTS | HDPE FACE - MINIMUM BEND RADIUS 5D UNLESS OTHERWISE SPECIFIED BY ENGINEER
R3 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1600/3 FF | SELECT FROM SABS 1123
R5 | All sizes | All Joints | CS, Flanges to SABS 1123 T4000 | Select from SABS 1123
V3 | ALL SIZES | MECH. JOINTS | CS FLANGES TO SABS 1123 T1600/3 FF | SELECT FROM SABS 1123
V3 | ALL SIZES | MECH. JOINTS | CS FLANGES TO SABS 1123 T1600/4 FF (FOR HOSE COUPLINGS) | SELECT FROM SABS 1123
V3 | ALL SIZES | PERM. JOINTS | BW
V4 | 65&UNDER | MECH. JOINTS | CS FLANGES TO SABS 1123 T2500/4 RF | SELECT FROM SABS 1123
V4 | 80&ABOVE | MECH. JOINTS | CS FLANGES TO SABS 1123 T2500/3 RF | SELECT FROM SABS 1123
V4 | 65&UNDER | PERM. JOINTS | SCRD AND SKTD TO BSP
V4 | 80&ABOVE | PERM. JOINTS | BW
BF3 | 125-250 | ALL JOINTS | CS, FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
BF3 | 300 | ALL JOINTS | CS, FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CF2 | 200-250 | ALL JOINTS | CS, FLANGES TO BS 4504 TABLE 64/3 RF | SABS 1431 GRADE 300W
CF2 | 300-400 | ALL JOINTS | CS, FLANGES TO BS4504 TABLE 40/3 RF | SABS 1431 GRADE 300W
CF3 | 200 | ALL JOINTS | CS, FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CF3 | 250-350 | ALL JOINTS | CS, FLANGES TO BS4504 TABLE 64/3 RF | SABS 1431 GRADE 300W
CF3 | 400 | ALL JOINTS | CS, FLANGES TO BS4504 TABLE 40/3 RF | SABS 1431 GRADE 300W
CF6 | 250 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
CF6 | 300-400 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CL2 | 200-250 | ALL JOINTS | CS, FLANGES TO BS 4504 TABLE 64/3 RF | SABS 1431 GRADE 300W
CL2 | 300-400 | ALL JOINTS | CS, FLANGES TO BS4504 TABLE 40/3 RF | SABS 1431 GRADE 300W
CL5 | 200 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
CL5 | 250-350 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
CL5 | 400 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 64/3 RF | SABS 1431 GRADE 300W
CL6 | 250 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 160/3 RF | SABS 1431 GRADE 300W
CL6 | 300-400 | ALL JOINTS | CS FLANGES TO BS 4504 TABLE 100/3 RF | SABS 1431 GRADE 300W
JG | 6-16 | MECH. JOINTS | ADAPTOR WITH ISO 228/1 MALE THREAD | PTFE - TEFLON
JG | 6-16 | MECH. JOINTS | ADAPTOR WITH ISO 228/1 FEMALE THREAD | PTFE - TEFLON
A3 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1600/3 FF | SELECT FROM SABS 1123
B3 | 50-150 | ALL JOINTS | CS, FLANGES TO STD DRG JAA00045203 SHT 1 | BS 4360 GRD 43A | JAA00045203
C3 | 200-450 | ALL JOINTS | CS, FLANGES TO STD DRG JAA00045204 SHT 1 | BS 4360 GRD 43A | JAA00045204
C5 | 200-450 | ALL JOINTS | CS, FLANGES TO STD DRG JAA00045204 SHT 3 | BS 4360 GRD 43A | JAA00045204
C7 | 200-450 | ALL JOINTS | CS, FLANGES TO STD DRG JAA00045204 SHT 5 | BS 4360 GRD 43A | JAA00045204
E7 | 200-500 | PERMANENT JOINTS | CS, SLEEVES (SEE NOTE 6) | SABS 719 GRADE "B" OR EQUIVALENT | JAA00045313
E7 | 200 | MECHANICAL JOINTS | CS, FLANGES TO BS 4504 T160/3 | SABS 1431 GRADE 300 WA
E7 | 250-350 | MECHANICAL JOINTS | CS, FLANGES TO BS 4504 T100/3 | SABS 1431 GRADE 300 WA
E7 | 400 | MECHANICAL JOINTS | CS, FLANGES TO BS 4504 T64/3 | SABS 1431 GRADE 300 WA
E8 | 200-500 | PERMANENT JOINTS | CS, SLEEVES (SEE NOTE 6) | SABS 719 GRADE "B" OR EQUIVALENT | JAA00045313
E8 | 250-400 | MECHANICAL JOINTS | CS, FLANGES TO BS 4504 T100/3 | SABS 1431 GRADE 300 WA
J2 | ALL SIZES | MECH. JOINTS | POLYPROPYLENE STUB FLANGE WITH CS BACKING RING TO STD DRG JAA00045308 SHEETS 4 AND 5 | SELECT FROM SABS 1123 TABLE 1000 | JAA00045308
J2 | 16-110 | PERM. JOINTS | POLYPROPYLENE CONNECTOR TO STD DRG JAA00045308 SHEET 3 |  | JAA00045308
J2 | 125-500 | PERM. JOINTS | BW
L2 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T1000/3 | SELECT FROM SABS 1123
Q1 | 15-80 | ALL JOINTS | NYLON INSERT COUPLING TYPE 431
R6 | 65-700 | MECH. JOINTS | CS FLANGES TO SABS 1123 1600/3 FF | SELECT FROM SABS 1123
R6 | 65-700 | PERM. JOINTS | NO PERMANENT JOINTS - ALL FLANGED
R7 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T4000/3 FF | SELECT FROM SABS 1123
R8 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T4000/3 FF | SELECT FROM SABS 1123
R9 | ALL SIZES | ALL JOINTS | CS, FLANGES TO SABS 1123 T2500/3 FF | SELECT FROM SABS 1123
S2 | ALL SIZES | MECH. JOINTS | SS, FLANGES TO SABS 1123 T1000/3 FF | ASTM A240 316L
S2 | ALL SIZES | PERM. JOINTS | BW
T2 | 20-50 | ALL JOINTS | CS FLANGES, SABS 1123 TABLE 4000/3 RF, WELDNECK | SABS 1431 GRADE 300W
V2 | 50&UNDER | MECH. JOINTS | MI UNIONS, BRONZE TAPER SEAT, SCR'D TO BSP. SEE NOTE 5 | SABS 509
V2 | 65-700 | MECH. JOINTS | CS FLANGES TO SABS 1123 TABLE 1000/4 F.F. (SEE NOTE 4) | SELECT FROM SABS 1123
V2 | 65-700 | MECH. JOINTS | CS FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
V2 | 50&UNDER | PERM. JOINTS | SCR'D & SKTD TO BSP | SEE NOTE 2
V2 | 65-700 | PERM. JOINTS | BW
V2A | 50 | MECH. JOINTS | CS FLANGES TO SABS 1123 T1000/3 FF | SELECT FROM SABS 1123
V2A | 50 | PERM. JOINTS | BW
V5 | 65&UNDER | MECH. JOINTS | CS FLANGES TO SABS 1123 T4000/4 RF | SELECT FROM SABS 1123
V5 | 80&ABOVE | MECH. JOINTS | CS FLANGES TO SABS 1123 T4000/3 RF | SELECT FROM SABS 1123
V5 | 65&UNDER | PERM. JOINTS | SCRD AND SKTD TO BSP | SEE NOTE 1
V5 | 80&ABOVE | PERM. JOINTS | BW
V7 | 50&UNDER | MECH. JOINTS | WROUGHT STEEL UNIONS, SCR'D TO BSP. SEE NOTE 5 | BS 1740
V7 | 65-150 | MECH. JOINTS | CS FLANGES TO SABS 1123 TABLE 1000/4 F.F. (SEE NOTE 4) | SELECT FROM SABS 1123
V7 | 65-700 | MECH. JOINTS | CS FLANGES TO SABS 1123 1000/3 FF | SELECT FROM SABS 1123
V7 | 50&UNDER | PERM. JOINTS | SCR'D & SKTD TO BSP (BS 1740) | SEE NOTE 2
V7 | 65-700 | PERM. JOINTS | BW
X2 | 25-50 | ALL JOINTS | SEE NOTE 2
X3 | 50-150 | ALL JOINTS | QUICK RELEASE CLAMP TO STD DRG JAA00045312 SHEET 1 | FORGED STEEL | JAA00045312